## Hmi Tags
Name | DataType | Address | Comment [en-GB] | Acquisition mode | Acquisition cycle
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_PID_FLOW_3 | Real | %DB40.DBD288 | STOKER PID AIR FLOW POINT 3 | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.PUSH_FLOOR.OBSTR_COUNT | Real | %DB42.DBD960 | CP2 PUSH FLOOR OBSTRUCTION COUNTER VALUE | Cyclic in operation | 1 s
DB SEND/RECV COOLER 2.SEND.GENERAL.REMOTE_AUTO | Bool | %DB162.DBX70.6 | 0 = REMOTE MANUAL / 1 = REMOTE AUTO | Cyclic in operation | 1 s
DB PROCESS VALUES.EMISSIONS.PRESSURE_hPa | Real | %DB42.DBD856 | STACK AIR PRESSURE (hPa) | Continuous | 1 s
Stoker3Curves_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB MV TURB POWER METER.KW3 | Real | %DB202.DBD136 | ACTIVE POWER PHASE 3 (KW) | Cyclic in operation | 1 s
IDB CP13 FILT SCREW A DP.Load | Real | %DB547.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
IDB CP13 RS INCLIN SCREW.Rem_Cmds.RunFwd | Bool | %DB133.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.GENERAL.FORCE_AUTO | Bool | %DB1.DBX0.0 | FORCE AUTOMATIC MODE | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.EQUIP_STATUS.RC_TEMP_BEL_OIL_CUTOFF | Bool | %DB30.DBX13.7 | RESIDENCE CHAMBER IS BELOW OIL BURNER CUTOFF TEMPERATURE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_2TT06.LO | Real | %DB41.DBD2056 | LOW ALARM SETPOINT | Cyclic in operation | 1 s
IDB CP3 GRATE HYD PMP 2.Rem_Cmds.RunFwd | Bool | %DB116.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
IDB CP7 PLANT PUMP 2.Rem_Cmds.RunFwd | Bool | %DB188.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
IDB CP3 SCR CHN SLID VLV.Status.Direction | Bool | %DB105.DBX21.0 | Motor Running Direction (0 = Forward, 1 = Reverse) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 2.RECV.GENERAL.FANS_STATUS | Int | %DB162.DBW4 | COOLER FANS STATUS | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.LO.WORD4 | Int | %DB12.DBW56 | LOW ALARMS - WORD 4 | Continuous | 1 s
DB ALARM SETPOINTS.CP17_4LC02.HI | Real | %DB41.DBD1828 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
IDB TON SOOTB CYCLE INT.ET | Time | %DB2088.DBD8 | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.PID.PRIM_FAN.OP_MAX | Real | %DB40.DBD1372 | OUTPUT MAX VALUE (LMN_HLM) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.FUEL_DAMPER_OPN | Bool | %DB1.DBX6.6 | CP3 FUEL DAMPER MANUAL OPEN SELECT (SCADA) | Cyclic in operation | 1 s
IDB CP13 UREA SKID SYS.Rem_Cmds.RunFwd | Bool | %DB148.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_S245 | Bool | %DB45.DBX22.6 | CP13 RACK 4 RESIDUE SILO PRESSURE SWITCH | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.STOKER_2_MAN_MD | Bool | %DB1.DBX5.4 | CP3 STOKER 2 TRAVERSE MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
3Pw481_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SEND/RECV COOLER 5.SEND.GENERAL.REMOTE_AUTO | Bool | %DB165.DBX70.6 | 0 = REMOTE MANUAL / 1 = REMOTE AUTO | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT07.HIHI | Real | %DB41.DBD2240 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.TURBINE.COND_PMP_2_STAT | Int | %DB1.DBW118 | CONDENSATE PUMP 2 STATUS (0 = FAULT, 1 = STOPPED, 2 = RUNNING) | Cyclic in operation | 1 s
DB SETPOINTS.PID.TEMP_CTRL_STEAM_OUT.OP_MIN | Real | %DB40.DBD1606 | OUTPUT MIN VALUE (LMN_LLM) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MAIN_CTRL.AIR_FANS_START | Bool | %DB30.DBX1.3 | START COMBUSTION AIR FANS (FROM SCADA) | Cyclic in operation | 1 s
2CV07_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.POWER.SITE_IMPORT_EXPORT_KWh | DInt | %DB42.DBD1212 | SITE IMPORT / EXPORT POWER CONSUMPTION (kWh) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_3PI01a.HIHI | Real | %DB41.DBD960 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.ECONOM_2_EXT | Bool | %DB1.DBX20.0 | CP8 ECONOMISER SOOTBLOWER 2 MANUAL EXTEND SELECT (SCADA) | Cyclic in operation | 1 s
CP17 4CV04 ACTIVE | Bool | %M144.1 | CP17 DEAERATOR OVERFLOW VALVE ACTIVE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TT03.HIHI | Real | %DB41.DBD3392 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.FILTER.BS_HOPPER_VIB_OFF | Int | %DB40.DBW994 | BICARB HOPPER VIBRATOR OFF TIME (SEC) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.SEC_AIR_FLOW_CORR_FACT | Real | %DB40.DBD556 | SECONDARY AIR FLOW CORRECTION FACTOR | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.PUSH_FLOOR.CP2_LAD_1_INSERV | Bool | %DB1.DBX2.4 | CP2 PUSH FLOOR LADDER 1 IN SERVICE | Cyclic in operation | 1 s
ALARM ACTIVE | Bool | %M30.4 | SYSTEM ALARM ACTIVE | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_PID_FAN_SPD_OUT_4 | Real | %DB40.DBD64 | STOKER PID AIR FAN SPEED OUTPUT 4 | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FEED_LINE.CP18_K91 | Bool | %DB45.DBX8.2 | CP18 STOKER FUEL/FIRE DAMPER CONTROL VALVE 1CV05 | Cyclic in operation | 1 s
CP7 4PU01/02 SELECT | Bool | %M142.0 | CP7 BOILER FEED PUMP DUTY REQUEST (SCADA) (0=MAIN. 1=STANDBY) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2LT01.LO | Real | %DB41.DBD2664 | LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB SEND/RECV COOLER 5.RECV.GENERAL.PUMP_STATUS | Int | %DB165.DBW2 | COOLER PUMP STATUS | Cyclic in operation | 1 s
ALL EMSTOPS OK | Bool | %M40.0 | ALL EMERGENCY STOPS HEALTHY | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BURNER.RECIRC_DAMPER_OPN | Bool | %DB1.DBX38.3 | CP13 RECIRCULATION AIR DAMPER MANUAL OPEN SELECT (SCADA) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.BURN_PRESS_THRESHLD | Real | %DB40.DBD396 | COMBUSTION CHAMBER VACUUM (PRESSURE) FAULT THRESHOLD (mBar) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_3TI01d.HYST | Real | %DB41.DBD1168 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB MV TURB POWER METER.M6_PAC3200.I1 | Real | %DB202.DBD24 | CURRENT PHASE 1 (AMPS) | Cyclic in operation | 1 s
DB ALARMS.SYSTEM.WORD1.CP8_PSSu_HEALTHY | Bool | %DB11.DBX1.3 | CP8 SOOTBLOWER SAFETYBUS NODE HEALTHY (192.168.2.108) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 2.RECV.ADIABATIC.STATUS | Int | %DB162.DBW30 | ADIABATIC SYSTEM STATUS | Cyclic in operation | 1 s
IDB PLC.PLC.LEDs.RUN | Bool | %DB2.DBX52.2 | CPU Running Status | Cyclic in operation | 1 s
DB SETPOINTS.PID.PRESS_CTRL_STEAM_OUT.OP_SCALE | Real | %DB40.DBD1656 | OUTPUT SCALE FACTOR (LMN_FAC) | Cyclic in operation | 1 s
DB LV GEN POWER METER.M5_PAC3200.HZ | Real | %DB201.DBD84 | FREQUENCY (HZ) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_SPD_MAX | Real | %DB40.DBD128 | STOKER MAXIMUM SPEED | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP13R4_3TI01a | Real | %DB42.DBD124 | CP13 RACK 4 FILTER 1 INLET AIR TEMPERATURE (4..20mA = -50 - +300ºC) | Cyclic in operation | 1 s
DB SETPOINTS.PID.BICARB_FEED.OP_SCALE | Real | %DB40.DBD1794 | OUTPUT SCALE FACTOR (LMN_FAC) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.SPRHEAT_1_RET | Bool | %DB1.DBX18.2 | CP8 SUPERHEATER SOOTBLOWER 1 MANUAL RETRACT SELECT (SCADA) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD3.CP13R4_3PI01b | Bool | %DB11.DBX12.2 | CP13 RACK 4 FILTER 2 INLET PRESSURE | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD2.CP13R4_3PI01a | Bool | %DB11.DBX11.6 | CP13 RACK 4 FILTER 1 INLET PRESSURE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4TT01.LO | Real | %DB41.DBD1896 | LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.BOILER_FEED_WATER_VLV.CURR_SP | Real | %DB42.DBD1592 | CURRENT RAMP SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.PID.STOKER_1.RAMP_EN | Bool | %DB40.DBX1480.2 | RAMP ENABLED (1=ENABLED) | Cyclic in operation | 1 s
DB ALARMS TO SCADA.SUPPLIES.WORD2 | Int | %DB12.DBW88 | POWER SUPPLY ALARMS - WORD 2 | Continuous | 1 s
2CV02TempPID_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP17_4FT01 | Real | %DB42.DBD244 | CP17 FEEDWATER FLOWMETER (4-20mA = 0-25 t/Hr) | Cyclic in operation | 1 s
IDB GR HYD PUMP 2 PBUS.Send.ControlWord | Word | %DB504.DBW8 | Control Word | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_PRDS_CTRL.MANUAL_VAL | Real | %DB40.DBD1178 | PID OUTPUT IN MANUAL (MAN) | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD6.CP3_CHEM_TANK_3_LVL_LO | Bool | %DB11.DBX114.7 | CP3 HIGH PRESSURE PUMP CHEMICAL TANK LEVEL LOW ALARM | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.BICARB_FEED.OUTPUT | Real | %DB42.DBD1968 | OUTPUT VALUE | Cyclic in operation | 1 s
ID FAN OK AUTOSTART | Bool | %M106.0 | ID FAN READY / AVAILABLE FOR SYSTEM AUTO START | Cyclic in operation | 1 s
CP2 PUSH FLR AT FWD | Bool | %M54.5 | CP2 PUSH FLOOR FULLY FORWARD DETECTED | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_45 | Bool | %DB2.DBX299.4 | Profibus Node | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK3.BEARING_TEMP_10 | DInt | %DB400.DBD136 | TURBINE BEARING TEMPERATURE POS 84.10 DEG C (x100) | Cyclic in operation | 1 s
IDB CP13 PAC AGITATOR.Rem_Cmds.RemoteCtrl | Bool | %DB143.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SEND/RECV COOLER 5.SEND.TIMES.MIN_RUN_TIME | Time | %DB165.DBD214 | COOLER MINIMUM RUN TIME | Cyclic in operation | 1 s
DB LV GEN POWER METER.M5_PAC3200.PF1 | Real | %DB201.DBD72 | POWER FACTOR PHASE 1 | Cyclic in operation | 1 s
IDB CP13 FILT DISCH FAN.Status.StatusWord | Int | %DB130.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.HIHI.WORD7 | Int | %DB12.DBW34 | HIGH HIGH ALARMS - WORD 7 | Continuous | 1 s
DB SETPOINTS.TIMERS.BURNER.BURN_PRESS_ALM | Int | %DB40.DBW938 | COMBUSTION CHAMBER VACUUM (PRESSURE) ALARM FAULT THRESHOLD TIME (SEC) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.FILTER.RES_SILO_ARM_EXT | Bool | %DB1.DBX29.3 | RESIDUE SILO ARM MANUAL EXTEND SELECT (SCADA) | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.FILTER.BH_VIB_STAT | Int | %DB1.DBW246 | BICARB HOPPER VIBRATOR STATUS | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.STOP.TIMERS.LEV_SCREW_1MTR02 | S5Time | %DB30.DBW114 | LEVELLING SCREW | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.TURBINE_2.CURR_L1 | Real | %DB42.DBD1424 | CURRENT L1 | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2SW11 | Bool | %DB45.DBX12.6 | CP8 ECONOMISER SOOTBLOWER 2 RETRACTED PROXIMITY SWITCH | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_PID_FLOW_OUT_1 | Real | %DB40.DBD92 | STOKER PID AIR FLOW OUTPUT 1 | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD2.CP13R4_8LO01 | Bool | %DB11.DBX11.5 | CP13 RACK 4 BICARB SILO LOAD CELL WEIGHT | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.START.TIMERS.UREA_SKID | S5Time | %DB30.DBW158 | UREA DeNOx SKID | Cyclic in operation | 1 s
CP1 M4 PAC3200 RX OK | Bool | %M200.0 | CP1 DATA RECEIVED OK FROM M4 LV GRID POWER METER | Cyclic in operation | 1 s
IDB ST HYD PUMP 1 PBUS.Control.RefSpeed | Real | %DB500.DBD32 | Drive Speed Reference in Percentage (%) | Cyclic in operation | 1 s
IDB CP13 FILTER SCREW B.Status.StatusWord | Int | %DB127.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_OBSTR_PRESET | Real | %DB40.DBD24 | STOKER 2 OBSTRUCTION ALARM COUNTER PRESET | Cyclic in operation | 1 s
IDB CP13 FILTER SEAL B.Rem_Cmds.RunFwd | Bool | %DB129.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.ECONOM_3_RET | Bool | %DB1.DBX20.4 | CP8 ECONOMISER SOOTBLOWER 3 MANUAL RETRACT SELECT (SCADA) | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_PRDS_CTRL.GAIN | Real | %DB40.DBD1182 | P TERM (GAIN) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_PID_FLOW_4 | Real | %DB40.DBD292 | STOKER PID AIR FLOW POINT 4 | Cyclic in operation | 1 s
8MTR07_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.BURNER.CP18_K96 | Bool | %DB45.DBX14.6 | CP18 MOVING GRATE 2 FORWARD SOLENOID 1CV18 (LOWER LEFT) | Cyclic in operation | 1 s
11RMC4F_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP7_U75.LO | Real | %DB41.DBD584 | LOW ALARM SETPOINT | Cyclic in operation | 1 s
IDB BICARB FEEDER PBUS.Status.ErrorCode | Int | %DB516.DBW46 | Last Trip Code | Cyclic in operation | 1 s
DB SETPOINTS.PID.TEMP_CTRL_STEAM_OUT.MAN_AUTO | Bool | %DB40.DBX1618.0 | PID MANUAL/AUTO MODE (1=MANUAL) (MAN_ON) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.START.BITS.ED_CURR_SEP_1GR01 | Bool | %DB30.DBX74.1 | EDDY CURRENT SEPARATOR | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK2.BEARING_TEMP_1 | DInt | %DB400.DBD100 | TURBINE BEARING TEMPERATURE POS 84.1 DEG C (x100) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BURNER.GRATE_2_MAN_MD | Bool | %DB1.DBX37.4 | CP3 GRATE 2 TRAVERSE MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
IDB CP13 BS AGITATOR.Rem_Cmds.RemoteCtrl | Bool | %DB139.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.SOOTBLOWERS.SOOTB_INTERVAL | Int | %DB40.DBW1010 | INTERVAL TIMER BETWEEN SOOTBLOWERS (x10 SEC) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_8IN02.LO | Real | %DB41.DBD1224 | LOW ALARM SETPOINT | Cyclic in operation | 1 s
8CS01_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB MV TURB POWER METER.KVAr1 | Real | %DB202.DBD140 | REACTIVE POWER PHASE 1 (KVAr) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_PID_FLOW_5 | Real | %DB40.DBD296 | STOKER PID AIR FLOW POINT 5 | Cyclic in operation | 1 s
IDB CP3 DISTRIB SCREW DP.Load | Real | %DB541.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP19_2PT03 | Real | %DB42.DBD344 | CP19 SUPERHEATER 2 STEAM OUTLET PRESSURE (4-20mA = 0-63 Bar) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2PT03.HYST | Real | %DB41.DBD2768 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2SW06 | Bool | %DB45.DBX11.3 | CP8 BOILER SOOTBLOWER 1 EXTENDED PROXIMITY SWITCH | Cyclic in operation | 1 s
DB ALARMS TO SCADA.COOLERS.COOLER5.WORD1 | Int | %DB12.DBW146 | COOLER 5 ALARMS - WORD 1 | Continuous | 1 s
DB SYSTEM CONTROL.FILTER.GENERAL.START_COND | Bool | %DB30.DBX144.3 | STARTING CONDITIONS | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.SOOTB_CYCLE_TMR_EN | Bool | %DB1.DBX21.7 | SOOTBLOWERS CYCLE TIMER ENABLE (SCADA) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.OP_MODES.OP_MODE_3 | Bool | %DB30.DBX8.3 | SYSTEM IN OPERATION MODE 3 (PRE-HEAT) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_1FT03.HYST | Real | %DB41.DBD1424 | ALARM HISTERESYS | Cyclic in operation | 1 s
IDB FEED PUMP 2 PBUS.Send.ControlWord | Word | %DB509.DBW8 | Control Word | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4PLT03.LOLO | Real | %DB41.DBD1996 | LOW LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_PID_FAN_SPD_5 | Real | %DB40.DBD256 | STOKER PID AIR FAN SPEED POINT 5 | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_PID_FAN_SPD_1 | Real | %DB40.DBD32 | STOKER PID AIR FAN SPEED POINT 1 | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_PID_FLOW_3 | Real | %DB40.DBD184 | STOKER PID AIR FLOW POINT 3 | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.DAMPERS.CP13R4_K288 | Bool | %DB45.DBX30.0 | CP13 RACK 4 OPEN PRIMARY AIR DAMPER | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.FILTER.RS_AIR_VLV_STAT | Int | %DB1.DBW232 | RESIDUE SILO AIR FLUIDISATION VALVE STATUS | Cyclic in operation | 1 s
IDB CP8 SPRHEAT SOOTBL 1.Status.StatusWord | Int | %DB117.DBW22 | Motor Status Word | Cyclic in operation | 1 s
STOP 1MTR10 | Timer | %T46 | CP3 DISTRIBUTION SCREW STOP DELAY TIMER | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK4.MAINS_VOLTAGE | DInt | %DB400.DBD216 | MAINS VOLTAGE | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_PID_FAN_SPD_OUT_1 | Real | %DB40.DBD52 | STOKER PID AIR FAN SPEED OUTPUT 1 | Cyclic in operation | 1 s
Stoker2PID_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.START.TIMERS.ASH_SYS | S5Time | %DB30.DBW152 | ASH CONVEYING AND STORAGE SYSTEM | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.STOKER_1_MAN_MD | Bool | %DB1.DBX5.0 | CP3 STOKER 1 TRAVERSE MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TT07.HI | Real | %DB41.DBD3268 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SEND/RECV COOLER 2.SEND.GENERAL.REMOTE_RUN | Bool | %DB162.DBX70.7 | 0 = STOP / 1 = RUN | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TT01.HI | Real | %DB41.DBD3012 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP13R4_3PI01b | Real | %DB42.DBD136 | CP13 RACK 4 FILTER 2 INLET PRESSURE (4..20mA = 0 - +50mBar) | Cyclic in operation | 1 s
DB SAFETY.RECV.CP7_ESPB_OK | Bool | %DB44.DBX2.5 | BOILER PANEL CP7 EM STOP P/BUTTON HEALTHY (1=HEALTHY) | Cyclic in operation | 1 s
DB MV TURB POWER METER.M6_PAC3200.PF3 | Real | %DB202.DBD80 | POWER FACTOR PHASE 3 | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_S2522 | Bool | %DB45.DBX20.7 | CP13 RACK 4 RESIDUE SILO SLEWING RING EXTENDED PROXIMITY | Cyclic in operation | 1 s
RecircFanPID_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP19_2LT01 | Real | %DB42.DBD332 | CP19 DP CELL WATER LEVEL (4-20mA = 140-1100 mm) | Cyclic in operation | 1 s
IDB CP13 FILT SEAL A DP.Status | Int | %DB549.DBW2 | Motor Status | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_S237 | Bool | %DB45.DBX22.4 | CP13 RACK 4 FILTER 1 HOPPER LEVEL PROBE | Cyclic in operation | 1 s
IDB CP13 FILTER SEAL A.Rem_Cmds.RunFwd | Bool | %DB128.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_3EM01.HYST | Real | %DB41.DBD2960 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4PT02.HIHI | Real | %DB41.DBD1920 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK5.ALARM106 | Bool | %DB400.DBX237.2 | OIL PUMP ON | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2PT01.LOLO | Real | %DB41.DBD2700 | LOW LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB LV GRID POWER METER.KW1 | Real | %DB200.DBD128 | ACTIVE POWER PHASE 1 (KW) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.SPRHEAT_2_RET | Bool | %DB1.DBX18.5 | CP8 SUPERHEATER SOOTBLOWER 2 MANUAL RETRACT SELECT (SCADA) | Cyclic in operation | 1 s
DB SETPOINTS.PID.PRIM_FAN.OP_MIN | Real | %DB40.DBD1376 | OUTPUT MIN VALUE (LMN_LLM) | Cyclic in operation | 1 s
IDB CP7 PLANT PUMP 2.Rem_Cmds.RemoteCtrl | Bool | %DB188.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.DAMPERS.CP13R4_S264 | Bool | %DB45.DBX30.4 | CP13 RACK 4 RECIRCULATION AIR DAMPER OPENED | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD6.CP3_CHEM_TANK_1_LVL_LO | Bool | %DB11.DBX114.5 | CP3 LOW PRESSURE PUMP 1 CHEMICAL TANK LEVEL LOW ALARM | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4PLT03.HI | Real | %DB41.DBD1988 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2PSZ02.HIHI | Real | %DB41.DBD2784 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK3.OP_HOURS | DInt | %DB400.DBD160 | OPERATING HOURS | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.VALVES.CP8_2SW15 | Bool | %DB45.DBX16.4 | CP8 STEAM STOP VALVE 2CV06 OPEN FEEDBACK | Cyclic in operation | 1 s
IDB ST HYD PUMP 2 PBUS.Recv.StatusWord | Word | %DB501.DBW20 | Status Word | Cyclic in operation | 1 s
DB ALARMS TO SCADA.PROCESS.WORD11 | Int | %DB12.DBW124 | PROCESS ALARMS - WORD 11 | Continuous | 1 s
DB PROCESS VALUES.MISCELLANEOUS.BURNER.SECOND_AIR_PID_SP | Real | %DB42.DBD1308 | SECONDARY AIR FAN PID CONTROLLER SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_2_PID_FLOW_2 | Real | %DB40.DBD492 | GRATE PID AIR FLOW POINT 2 | Cyclic in operation | 1 s
1MTR03_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_1_SPD_MAX | Real | %DB40.DBD476 | GRATE MAXIMUM SPEED | Cyclic in operation | 1 s
DB ALARMS TO SCADA.COOLERS.COOLER1.WORD2 | Int | %DB12.DBW132 | COOLER 1 ALARMS - WORD 2 | Continuous | 1 s
IDB CP13 FILT DIS FAN DP.Load | Real | %DB551.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
DB SETPOINTS.PID.UREA_FEED.MANUAL_VAL | Real | %DB40.DBD1822 | PID OUTPUT IN MANUAL (MAN) | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK2.BEARING_TEMP_B | DInt | %DB400.DBD88 | GENERATOR BEARING TEMPERATURE B DEG C (x100) | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK2.W_WIND_TEMP | DInt | %DB400.DBD76 | WINDING TEMPERATURE W DEG C (x100) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_2TT06.HI | Real | %DB41.DBD2052 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SEND/RECV COOLER 3.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_HIHI | Real | %DB163.DBD182 | CIRCULATION WATER OUTLET TEMPERATURE HIGH HIGH ALARM | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2MTR04_FWD | Bool | %DB45.DBX11.4 | CP8 BOILER SOOTBLOWER 2 MOTOR RUN FORWARD | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_PID_LAMBDA_MAX | Real | %DB40.DBD320 | STOKER PID AIR LAMBDA MAXIMUM SCALING VALUE | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.BOILER_FEED_WATER_VLV.RAMP_ACTV | Bool | %DB42.DBX1590.0 | RAMP ACTIVE | Cyclic in operation | 1 s
DB SEND/RECV COOLER 1.SEND.TIMES.ADIABATIC_MIN_RUN_TIME | Time | %DB161.DBD218 | COOLER ADIABATIC SYSTEM MINIMUM RUN TIME | Cyclic in operation | 1 s
1TT0234_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.GENERAL.FAULT_RESET | Bool | %DB1.DBX0.1 | FAULT RESET FROM SCADA | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD7.CP19_2TT03 | Bool | %DB11.DBX21.2 | CP19 SUPERHEATER 2 STEAM OUTLET TEMPERATURE | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.ECONOM_3_MD | Bool | %DB1.DBX20.2 | CP8 ECONOMISER SOOTBLOWER 3 MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP13R4_3TI01d | Real | %DB42.DBD144 | CP13 RACK 4 FILTER 2 OUTLET AIR TEMPERATURE (4..20mA = -50 - +300ºC) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.STOP.BITS.UREA_SKID | Bool | %DB30.DBX182.1 | UREA DeNOx SKID | Cyclic in operation | 1 s
IDB CP7 LP DOSING PMP1.Rem_Cmds.RemoteCtrl | Bool | %DB185.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SETPOINTS.PID.STOKER_1.OP_OFFSET | Real | %DB40.DBD1476 | OUTPUT OFFSET (LMN_OFF) | Cyclic in operation | 1 s
IDB CP13 BS BLOW SEAL.Status.StatusWord | Int | %DB142.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD3.CP19_2CV01_TIMEOUT | Bool | %DB11.DBX109.2 | CP19 SUPERHEATER 2 STEAM OUTLET MAIN STOP VALVE TIMEOUT ALARM | Cyclic in operation | 1 s
IDB PRIM AIR FAN PBUS.Send.ControlWord | Word | %DB513.DBW8 | Control Word | Cyclic in operation | 1 s
IDB CP7 LP DOSING PMP1.Status.StatusWord | Int | %DB185.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB ALARMS TO SCADA.COOLERS.COOLER6.WORD2 | Int | %DB12.DBW152 | COOLER 6 ALARMS - WORD 2 | Continuous | 1 s
IDB CP2 LEV AUGER.Rem_Cmds.RunFwd | Bool | %DB103.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.FILTER.ID_FAN_VENTIL_PID_SP | Real | %DB40.DBD684 | ID FANS PID SETPOINT IN VENTILATION OPERATION | Cyclic in operation | 1 s
User Group Number | Int | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.HI.WORD4.CP17_4LC02 | Bool | %DB11.DBX43.1 | CP17 DEAERATOR WATER LEVEL TRANSDUCER (4-20mA = 0-100%) | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_PUMP.RAMP_EN | Bool | %DB40.DBX1894.2 | RAMP ENABLED (1=ENABLED) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP12_EXH_PRESS.LO | Real | %DB41.DBD3464 | LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD2.STK_3_JAMMED | Bool | %DB11.DBX107.0 | CP3 STOKER 3 JAMMED ALARM | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_2FT01.HYST | Real | %DB41.DBD2032 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB SEND/RECV COOLER 2.SEND.GENERAL.START_COOLER | Bool | %DB162.DBX70.5 | <No Value> | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.HIHI.WORD4.CP17_8LT04 | Bool | %DB11.DBX28.3 | CP17 TREATED WATER TANK LEVEL TRANSDUCER (4-20mA = 0-100%) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD6.CP19_2TSZ03 | Bool | %DB11.DBX18.1 | CP19 TEMPERATURE SWITCH AFTER SUPERHEATER 2 | Cyclic in operation | 1 s
IDB ID FAN B PBUS.Send.ControlWord | Word | %DB512.DBW8 | Control Word | Cyclic in operation | 1 s
Stoker1Curves_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.PID.STOKER_3.MANUAL_VAL | Real | %DB40.DBD2006 | PID OUTPUT IN MANUAL (MAN) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.STOP.BITS.PAC_DOSING | Bool | %DB30.DBX182.0 | P.A.C. DOSING SYSTEM | Cyclic in operation | 1 s
IDB CP13 FILT SEAL B DP.Status | Int | %DB550.DBW2 | Motor Status | Cyclic in operation | 1 s
DB SETPOINTS.PID.HI_PRESS_CTRL_STEAM.OP_MIN | Real | %DB40.DBD1560 | OUTPUT MIN VALUE (LMN_LLM) | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP19_2TT03 | Real | %DB42.DBD424 | CP19 SUPERHEATER 2 STEAM OUTLET TEMPERATURE (4-20mA = 0-450 ºC) | Cyclic in operation | 1 s
DB ALARMS TO SCADA.COOLERS.COOLER4.WORD2 | Int | %DB12.DBW144 | COOLER 4 ALARMS - WORD 2 | Continuous | 1 s
IDB CP13 BS BLOW SEAL DP.Status | Int | %DB554.DBW2 | Motor Status | Cyclic in operation | 1 s
IDB PLC.PLC.LEDs.SF | Bool | %DB2.DBX52.0 | CPU System Fault Status | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.TURBINE.SPEED | Real | %DB42.DBD1112 | TURBINE SPEED | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.RC_UREA_TEMP | Real | %DB40.DBD408 | RESIDENCE CHAMBER MIN TEMPERATURE FOR UREA INJECTION (DEG C) | Cyclic in operation | 1 s
DB ALARMS TO SCADA.COOLERS.COOLER6.WORD1 | Int | %DB12.DBW150 | COOLER 6 ALARMS - WORD 1 | Continuous | 1 s
DB SEND/RECV COOLER 1.RECV.PROCESS_VALUES.CIRC_WATER_OUT_TEMP | Real | %DB161.DBD22 | CIRCULATION WATER OUTLET TEMPERATURE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_SPARE1.HIHI | Real | %DB41.DBD1056 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.PID.ID_FAN.MAN_AUTO | Bool | %DB40.DBX1296.0 | PID MANUAL/AUTO MODE (1=MANUAL) (MAN_ON) | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.FILTER.SCREW_2_ON_TIME | Int | %DB40.DBW998 | FILTER DISCHARGE SCREW 2 ON TIME | Cyclic in operation | 1 s
DB LV GEN POWER METER.KW2 | Real | %DB201.DBD132 | ACTIVE POWER PHASE 2 (KW) | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.WOOD_FEED.WOOD_FEED_TIMEOUT_TRIP | Int | %DB40.DBW894 | WOOD FEED TIMEOUT TRIP TIME (SEC) | Cyclic in operation | 1 s
WOOD FEED TOUT ALM TMR | Timer | %T177 | WOOD FEED TIMEOUT ALARM TIMER | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TT02.HIHI | Real | %DB41.DBD3040 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
BS HOP VIBRATOR ACTIVE | Bool | %M118.3 | BICARB SILO HOPPER VIBRATOR ACTIVE | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FEED_LINE.CP3_1MTR04_FWD | Bool | %DB45.DBX6.0 | CP3 SLIDE VALVE MOTOR RUN FORWARD | Cyclic in operation | 1 s
DB ALARMS.COOLERS.COOLER6.WORD2.COMMS_FAULT | Bool | %DB11.DBX152.0 | COMMUNICATION FAULT | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK5.ALARM105 | Bool | %DB400.DBX237.1 | ELECTRICAL TRIP | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_PID_FAN_SPD_2 | Real | %DB40.DBD244 | STOKER PID AIR FAN SPEED POINT 2 | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.OUTPUTS.CP17_4CV05_REF | Real | %DB42.DBD628 | CP17 CONTROL VALVE FEED WATER TO PRDS REFERENCE POSITION (4-20mA = 0-100%) | Cyclic in operation | 1 s
IDB CP13 BS BLOW SEAL DP.Load | Real | %DB554.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP7_7TT06.LO | Real | %DB41.DBD648 | LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_PID_FLOW_OUT_4 | Real | %DB40.DBD312 | STOKER PID AIR FLOW OUTPUT 4 | Cyclic in operation | 1 s
IDB CP13 FILTER SCREW B.Rem_Cmds.RunFwd | Bool | %DB127.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_SPD_FACTOR | Real | %DB40.DBD228 | STOKER SPEED FACTOR | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BURNER.BRN_LOW_TEMP_IN_USE | Bool | %DB1.DBX38.4 | RESIDANCE CHAMBER LOWEST TEMPERATURE PROBE VALUE IN USE | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.EQUIP_STATUS.FEED_IS_OFF | Bool | %DB30.DBX12.0 | FEED SYSTEM IS OFF (NO WOOD FEED) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1PT01.HIHI | Real | %DB41.DBD2432 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_8LT01.HYST | Real | %DB41.DBD1616 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TSZ01.HIHI | Real | %DB41.DBD2624 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
IDB CP13 FILTER SEAL B.Status.StatusWord | Int | %DB129.DBW22 | Motor Status Word | Cyclic in operation | 1 s
WID ALARM OCC | Bool | %M303.0 | 30 MIN 97% WID LIMIT ALARM OCCURRED | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_10 | Bool | %DB2.DBX295.1 | Profibus Node | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_PID_FAN_SPD_OUT_3 | Real | %DB40.DBD268 | STOKER PID AIR FAN SPEED OUTPUT 3 | Cyclic in operation | 1 s
IDB REC AIR FAN PBUS.Control.RefSpeed | Real | %DB515.DBD40 | Drive Speed Reference in Percentage (%) | Cyclic in operation | 1 s
DB SAFETY.RECV.WOOD_ESR_OK | Bool | %DB44.DBX0.1 | Wood Feed Emergency Stop Healthy (1=healthy) | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_4 | Bool | %DB2.DBX294.3 | Profibus Node | Cyclic in operation | 1 s
DB LV GRID POWER METER.KVAtot | Real | %DB200.DBD152 | TOTAL APPARANT POWER (KVA) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.SPRHEAT_2_MD | Bool | %DB1.DBX18.3 | CP8 SUPERHEATER SOOTBLOWER 2 MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
8VAS01_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.PUSH_FLOOR.TRAV_MAN_ST | Bool | %DB1.DBX2.1 | CP2 PUSH FLOOR TRAVERSE MANUAL START SELECT (SCADA) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MAIN_CTRL.OP_MODE_0_SEL | Bool | %DB30.DBX0.4 | OP MODE 0 (SHUTDOWN) REQUEST (FROM SCADA) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.STOP.TIMERS.HYD_PWR_PACK_1MTR01 | S5Time | %DB30.DBW118 | HYDRAULIC POWER PACK | Cyclic in operation | 1 s
DB MV TURB POWER METER.KVAr2 | Real | %DB202.DBD144 | REACTIVE POWER PHASE 2 (KVAr) | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.BURNER.BRN_VACUUM_SENS_SEL | Int | %DB1.DBW138 | BURNER VACUUM SENSOR DUTY SELECT (0 = BOTH, 1 = 1PT01, 2 = 1PT02) | Cyclic in operation | 1 s
DB PROCESS VALUES.EMISSIONS.NOx_Mg_m3 | Real | %DB42.DBD812 | OXIDES OF NITROGEN NOx (Mg/m3) | Continuous | 1 s
DB PROCESS VALUES.MISCELLANEOUS.TURBINE_2.CURR_L3 | Real | %DB42.DBD1432 | CURRENT L3 | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.PUSH_FLOOR.CP2_1SW35_MIN | Bool | %DB45.DBX3.5 | CP2 PUSH FLOOR LADDER No 6 MINIMUM PROXIMITY | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_43 | Bool | %DB2.DBX299.2 | Profibus Node | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP17_4CV02_POS | Real | %DB42.DBD220 | CP17 FEEDWATER CONTROL VALVE ACTUAL POSITION (4-20mA = 0-100%) | Cyclic in operation | 1 s
TRIP ACTIVE | Bool | %M30.5 | SYSTEM TRIP ACTIVE | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.FILTER.FILT1_OUT_GT_IN_ALM | Int | %DB40.DBW988 | FILTER 1 OUTLET TEMPERATURE GREATER THAN INLET TEMPERATURE ALARM TIME (SEC) | Cyclic in operation | 1 s
IDB FEED PUMP 2 PBUS.Status.ActualSpeed | Real | %DB509.DBD38 | Actual Speed in Percentage (%) | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.TURBINE_2.EXT_PRESS | Real | %DB42.DBD1404 | EXTRACTION STEAM PRESSURE | Cyclic in operation | 1 s
DB SEND/RECV COOLER 1.SEND.SETPOINTS.FANS_SPEED_MANUAL | Real | %DB161.DBD110 | FANS SPEED FOR REMOTE MANUAL MODE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4PT01.HYST | Real | %DB41.DBD1744 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB ALARMS.SYSTEM.WORD1.CP2_PSSu_HEALTHY | Bool | %DB11.DBX1.2 | CP2 PUSHFLOOR SAFETYBUS NODE HEALTHY (192.168.2.102) | Cyclic in operation | 1 s
DB ALARMS TO SCADA.COOLERS.COOLER2.WORD1 | Int | %DB12.DBW134 | COOLER 2 ALARMS - WORD 1 | Continuous | 1 s
IDB PLC.Profibus.Nodes.Node_8 | Bool | %DB2.DBX294.7 | Profibus Node | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_SB2b | Bool | %DB45.DBX21.5 | CP13 RACK 4 FILTER 2 INLET VALVE A CLOSED | Cyclic in operation | 1 s
IDB CP12 TURBINE COOLER.Status.StatusWord | Int | %DB172.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.POWER.EXPORTING_POWER | Bool | %DB1.DBX10.1 | SITE IS EXPORTING POWER (SCADA) | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK2.BEARING_TEMP_2 | DInt | %DB400.DBD104 | TURBINE BEARING TEMPERATURE POS 84.2 DEG C (x100) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.LOLO.WORD4.CP17_8LT01 | Bool | %DB11.DBX70.2 | CP17 PLANT WATER TANK LEVEL TRANSDUCER (4-20mA = 0-100%) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4PT02.HI | Real | %DB41.DBD1924 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB MV TURB POWER METER.M6_PAC3200.PF1 | Real | %DB202.DBD72 | POWER FACTOR PHASE 1 | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.START.BITS.ASH_SYS | Bool | %DB30.DBX148.1 | ASH CONVEYING AND STORAGE SYSTEM | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.BOILER_2_RET | Bool | %DB1.DBX19.3 | CP8 BOILER SOOTBLOWER 2 MANUAL RETRACT SELECT (SCADA) | Cyclic in operation | 1 s
DB SAFETY.RECV.OS13a_ESPB_OK | Bool | %DB44.DBX2.6 | FILTER OPERATOR STATION OS13a EM STOP P/BUTTON HEALTHY (1=HEALTHY) | Cyclic in operation | 1 s
CP7 8PU04 SELECTED | Bool | %M152.2 | CP7 STANDBY PLANT WATER PUMP DUTY SELECTED | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_PRDS_CTRL.SP | Real | %DB40.DBD1168 | INTERNAL SETPOINT | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD6.CP17_4CV02_TIMEOUT | Bool | %DB11.DBX114.1 | CP17 FEEDWATER CONTROL VALVE TIMEOUT ALARM | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP7_7PLT07.HIHI | Real | %DB41.DBD672 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.STK_2_PID_MTHD_2_SEL | Bool | %DB1.DBX7.7 | STOKER 2 PID CONTROLLER METHOD 2 SELECTED | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK3.BEARING_TEMP_8 | DInt | %DB400.DBD128 | TURBINE BEARING TEMPERATURE POS 84.8 DEG C (x100) | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP19_2TT07 | Real | %DB42.DBD408 | CP19 BLOWDOWN VESSEL TEMPERATURE (PT100) (???-??? ºC) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.SPRHEAT_2_EXT | Bool | %DB1.DBX18.4 | CP8 SUPERHEATER SOOTBLOWER 2 MANUAL EXTEND SELECT (SCADA) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_3PI01b.HIHI | Real | %DB41.DBD1088 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.FEED_WTR_TANK_PRDS_CTRL.RAMP_ACTV | Bool | %DB42.DBX1560.0 | RAMP ACTIVE | Cyclic in operation | 1 s
MODE 0 Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
FeedPumpPID_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.PID.BICARB_FEED.CYCLE_TIME | Int | %DB40.DBW1774 | SAMPLE TIME (CYCLE) | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.SOOTBLOWERS.SHEAT_2_NB_2 | Int | %DB40.DBW1028 | SUPERHEATER SOOTBLOWER 2 NUMBER 2 | Cyclic in operation | 1 s
DB ALARMS.REMOTE.WORD1.CP13d_A23_ALM | Bool | %DB11.DBX83.0 | CP13d 3MTR12a DUTY ALMIG BELT 22 AIR COMPRESSOR 1 ALARM | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TT03.LOLO | Real | %DB41.DBD3404 | LOW LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ESTOPS.WORD1 | Int | %DB12.DBW78 | EMERGENCY STOP ALARMS - WORD 1 | Continuous | 1 s
IDB CP7 SB FEED PUMP.Rem_Cmds.RemoteCtrl | Bool | %DB181.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BICARB_FEED.SO2_STOP_FEED | Real | %DB40.DBD800 | SO2 SETPOINT TO STOP BICARB FEEDING | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.BOILER_1_RET | Bool | %DB1.DBX19.0 | CP8 BOILER SOOTBLOWER 1 MANUAL RETRACT SELECT (SCADA) | Cyclic in operation | 1 s
IDB BICARB FEEDER PBUS.Recv.StatusWord | Word | %DB516.DBW20 | Status Word | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_30 | Bool | %DB2.DBX297.5 | Profibus Node | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_8LO01.LOLO | Real | %DB41.DBD940 | LOW LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.PID.BOILER_FEED_WATER_VLV.OP_MIN | Real | %DB40.DBD1238 | OUTPUT MIN VALUE (LMN_LLM) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.SECOND_AIR_FAN.O2_PID_LOAD_2 | Real | %DB40.DBD736 | SECONDARY AIR FAN PID CONTROLLER LOAD POINT 2 | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_1FT02.HIHI | Real | %DB41.DBD1344 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD6.CP19_2TSZ01 | Bool | %DB11.DBX18.2 | CP19 TEMPERATURE GUARD STEAM OUTLET SUPERHEATER 2 | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_8LO01.HI | Real | %DB41.DBD932 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BICARB_FEED.HCL_STOP_FEED | Real | %DB40.DBD792 | HCL SETPOINT TO STOP BICARB FEEDING | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.START.BITS.DISTRIB_SCREW_1MTR10 | Bool | %DB30.DBX74.2 | HOPPER DISTRIBUTION SCREW | Cyclic in operation | 1 s
DB SETPOINTS.PID.BICARB_FEED_HCL.OP_MIN | Real | %DB40.DBD2112 | OUTPUT MIN VALUE (LMN_LLM) | Cyclic in operation | 1 s
IDB ST HYD PUMP 3 PBUS.Status.ActualSpeed | Real | %DB502.DBD38 | Actual Speed in Percentage (%) | Cyclic in operation | 1 s
WOOD FEED TOUT TRIP TMR | Timer | %T37 | WOOD FEED TIMEOUT TRIP TIMER | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_K276 | Bool | %DB45.DBX22.1 | CP13 RACK 4 BICARB SILO MAINTENANCE BUTTERFLY VALVE OPEN SOLENOID 8VAS01 | Cyclic in operation | 1 s
IDB REC AIR FAN PBUS.Status.Load | Real | %DB515.DBD50 | Drive Load in Percentage (%) | Cyclic in operation | 1 s
DB ALARMS.ESTOPS.WORD2.CP19_2PSZ01 | Bool | %DB11.DBX80.2 | BOILER PANEL CP19 HI HI STEAM DRUM PRESSURE TRIP | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.OP_MODES.OP_MODE_8 | Bool | %DB30.DBX9.0 | SYSTEM IN OPERATION MODE 8 (SHUTDOWN 2 - BURN-OFF) | Cyclic in operation | 1 s
DB SETPOINTS.PID.HI_TEMP_CTRL_STEAM.MAN_AUTO | Bool | %DB40.DBX1526.0 | PID MANUAL/AUTO MODE (1=MANUAL) (MAN_ON) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FEED_LINE.CP18_1SW14 | Bool | %DB45.DBX8.0 | CP18 STOKER 3 FORWARD PROXIMITY SWITCH | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.ECONOM_1_RET | Bool | %DB1.DBX19.6 | CP8 ECONOMISER SOOTBLOWER 1 MANUAL RETRACT SELECT (SCADA) | Cyclic in operation | 1 s
DB SETPOINTS.PID.OIL_BURNER.OP_OFFSET | Real | %DB40.DBD1706 | OUTPUT OFFSET (LMN_OFF) | Cyclic in operation | 1 s
DB SETPOINTS.PID.STOKER_1.OP_SCALE | Real | %DB40.DBD1472 | OUTPUT SCALE FACTOR (LMN_FAC) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.PUSH_FLOOR.CP2_1SW23_MAX | Bool | %DB45.DBX3.2 | CP2 PUSH FLOOR LADDER No 4 MAXIMUM PROXIMITY | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MODE_STATUS.EXEC_OPMODE_7_STAT | Int | %DB30.DBW46 | EXECUTIVE OVERRIDE MODE 7 STATUS (0=NOT SEL, 1=REQ, 2=REQ & ACHIEVED) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.MAINS.CP1_VC2_P2_O102 | Bool | %DB45.DBX0.2 | CP1 TRANSFORMER AND L.V. SWITCH TRIP FROM CP1 | Cyclic in operation | 1 s
IDB CP13 FILTER SEAL A.Rem_Cmds.RemoteCtrl | Bool | %DB128.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
IDB CP7 LP DOSING PMP1.Rem_Cmds.RunFwd | Bool | %DB185.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.BURNER.COOLING_TIME_H | Int | %DB40.DBW944 | BURNER COOLING TIME PERIOD (COOLING - MODE 9) (HOURS) | Cyclic in operation | 1 s
IDB ID FAN A PBUS.Send.ControlWord | Word | %DB511.DBW8 | Control Word | Cyclic in operation | 1 s
DB SEND/RECV COOLER 5.RECV.ADIABATIC.STATUS | Int | %DB165.DBW30 | ADIABATIC SYSTEM STATUS | Cyclic in operation | 1 s
IDB ID FAN B PBUS.Status.ActualSpeed | Real | %DB512.DBD46 | Actual Speed in Percentage (%) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.STK_3_PID_MTHD_3_SEL | Bool | %DB1.DBX8.4 | STOKER 3 PID CONTROLLER METHOD 3 SELECTED | Cyclic in operation | 1 s
DB SETPOINTS.PID.TEMP_CTRL_STEAM_OUT.INTEGRAL | Int | %DB40.DBW1600 | I TERM (TI) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.MAINS.CP1_VC2_P2_O101 | Bool | %DB45.DBX0.1 | CP1 TRANSFORMER AND L.V. SWITCH ALARM FROM CP1 | Cyclic in operation | 1 s
DB SAFETY.RECV.CP19_2TSZ03 | Bool | %DB44.DBX4.3 | BOILER PANEL CP19 SUPERHEATER 2 HI HI OUTLET TEMP TRIP (1=HEALTHY) | Cyclic in operation | 1 s
IDFansPID_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_47 | Bool | %DB2.DBX299.6 | Profibus Node | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.OP_MODES.OP_MODE_1 | Bool | %DB30.DBX8.1 | SYSTEM IN OPERATION MODE 1 (AUTO OFF) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_S253 | Bool | %DB45.DBX23.2 | CP13 RACK 4 RESIDUE SILO HORIZONTAL DISCHARGE SCREW PRESSURE SWITCH | Cyclic in operation | 1 s
DB SAFETY.RECV.CR_LH_ESPB_OK | Bool | %DB44.DBX3.1 | CONTROL ROOM L/HAND EM STOP P/BUTTON HEALTHY (1=HEALTHY) | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP18_1TT05 | Real | %DB42.DBD272 | CP18 STOKER TEMPERATURE PROBE 1 (PT100) (0-150 ºC) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 4.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_HIHI | Real | %DB164.DBD182 | CIRCULATION WATER OUTLET TEMPERATURE HIGH HIGH ALARM | Cyclic in operation | 1 s
DB SETPOINTS.PID.STOKER_2.MANUAL_VAL | Real | %DB40.DBD1960 | PID OUTPUT IN MANUAL (MAN) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.GENERAL.ALL_EQUIP_AVAIL | Bool | %DB30.DBX144.1 | ALL FILTER EQUIPMENT AVAILABLE | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.FILTER.BS_BLOW_FAN_VLV_STAT | Int | %DB1.DBW248 | BICARB SILO BLOWING FAN VALVE STATUS | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.START.REQ | Bool | %DB30.DBX72.0 | FEED LINE STARTUP REQUEST | Cyclic in operation | 1 s
DB SETPOINTS.PID.TEMP_CTRL_STEAM_OUT.OP_OFFSET | Real | %DB40.DBD1614 | OUTPUT OFFSET (LMN_OFF) | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.LO.WORD1 | Int | %DB12.DBW50 | LOW ALARMS - WORD 1 | Continuous | 1 s
DB SCADA DATA.BIT_DATA.VALVES.CP8_2SW17 | Bool | %DB45.DBX16.1 | CP8 STEAM DRAIN VALVE 2CV05 OPEN FEEDBACK | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.PUSH_FLOOR.CP2_1SW34_MIN | Bool | %DB45.DBX3.3 | CP2 PUSH FLOOR LADDER No 5 MINIMUM PROXIMITY | Cyclic in operation | 1 s
DB SETPOINTS.PID.HI_PRESS_CTRL_STEAM.CYCLE_TIME | Int | %DB40.DBW1544 | SAMPLE TIME (CYCLE) | Cyclic in operation | 1 s
IDB ST HYD PUMP 1 PBUS.Status.ErrorCode | Int | %DB500.DBW46 | Last Trip Code | Cyclic in operation | 1 s
DB LV GEN POWER METER.KW1 | Real | %DB201.DBD128 | ACTIVE POWER PHASE 1 (KW) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2PSZ01.HIHI | Real | %DB41.DBD2560 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB PROCESS VALUES.EMISSIONS.HF_Mg_m3 | Real | %DB42.DBD836 | HYDROGEN FLUORIDE HF (Mg/m3) | Continuous | 1 s
DB MISCELLANEOUS.BITS.FILTER.FILTER2_IN_VLV_A_OPN | Bool | %DB1.DBX29.1 | CP13 FILTER 2 INLET VALVE A MANUAL OPEN SELECT (SCADA) | Cyclic in operation | 1 s
DB SETPOINTS.PID.ID_FAN.RAMP_EN | Bool | %DB40.DBX1296.2 | RAMP ENABLED (1=ENABLED) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TT03.HI | Real | %DB41.DBD3396 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
IDB CP7 LIFT PUMP 1.Status.StatusWord | Int | %DB182.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB SETPOINTS.PID.ID_FAN.OP_MIN | Real | %DB40.DBD1284 | OUTPUT MIN VALUE (LMN_LLM) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 4.SEND.TIMES.ADIABATIC_MIN_RUN_TIME | Time | %DB164.DBD218 | COOLER ADIABATIC SYSTEM MINIMUM RUN TIME | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_9 | Bool | %DB2.DBX295.0 | Profibus Node | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FEED_LINE.CP18_K931 | Bool | %DB45.DBX7.7 | CP18 STOKER 3 REVERSE RUN RELAY | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_14 | Bool | %DB2.DBX295.5 | Profibus Node | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_S2521 | Bool | %DB45.DBX20.6 | CP13 RACK 4 RESIDUE SILO SLEWING RING RETRACTED PROXIMITY | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_2_PID_FLOW_5 | Real | %DB40.DBD504 | GRATE PID AIR FLOW POINT 5 | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_1_SPD_OFFSET | Real | %DB40.DBD468 | GRATE SPEED OFFSET | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK5.ALARM61 | Bool | %DB400.DBX231.5 | CONDENSATE LEVEL MAX | Cyclic in operation | 1 s
DB SEND/RECV COOLER 6.RECV.GENERAL.WATCHDOG | Bool | %DB166.DBX0.0 | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.SOOTBLOWERS.ECON_2_NB_2 | Int | %DB40.DBW1036 | ECONOMISER SOOTBLOWER 2 NUMBER 2 | Cyclic in operation | 1 s
IDB PLC.DateTime.PLC.DateTime | Date_And_Time | %DB2.DBX8.0 | Date/time PLC | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.PRIM_FAN.CURR_SP | Real | %DB42.DBD1682 | CURRENT RAMP SETPOINT | Cyclic in operation | 1 s
10RMC1F_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
3MTR05_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SEND/RECV COOLER 4.RECV.ADIABATIC.STATUS | Int | %DB164.DBW30 | ADIABATIC SYSTEM STATUS | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.FUEL_DAMPER_MD | Bool | %DB1.DBX6.5 | CP3 FUEL DAMPER MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.EQUIP_STATUS.FEED_IS_ON | Bool | %DB30.DBX14.1 | FEED DISTRIBUTION SCREW IS RUNNING (FEEDING WOOD) | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD1.CP2_SCR_CHN_TENSION | Bool | %DB11.DBX105.1 | CP2 SCRAPER CHAIN CONVEYOR TENSIONER ALARM | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.FILTER.FILTER1_IN_VLV_B_OPN | Bool | %DB1.DBX28.7 | CP13 FILTER 1 INLET VALVE B MANUAL OPEN SELECT (SCADA) | Cyclic in operation | 1 s
CP8 ALL SOOTB RETRACTED | Bool | %M88.6 | CP8 ALL SOOTBLOWERS RETRACTED | Cyclic in operation | 1 s
IDB SCND AIR FAN PBUS.Status.Load | Real | %DB514.DBD50 | Drive Load in Percentage (%) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 3.RECV.GENERAL.FANS_STATUS | Int | %DB163.DBW4 | COOLER FANS STATUS | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD6.CP19_3EM01 | Bool | %DB11.DBX19.4 | CP13 RACK 4 FLUE GAS OXYGEN LEVEL | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.EMISSIONS.WID_LIMIT_SP_HRS | Int | %DB40.DBW928 | SETPOINT FOR WOOD FEED SUSPENSION DUE TO WID LIMIT EXCEEDED (HOURS) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 4.SEND.SETPOINTS.FANS_SPEED_MANUAL | Real | %DB164.DBD110 | FANS SPEED FOR REMOTE MANUAL MODE | Cyclic in operation | 1 s
IDB SCND AIR FAN PBUS.Status.ErrorCode | Int | %DB514.DBW54 | Last Trip Code | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.SPRHEAT_1_EXT | Bool | %DB1.DBX18.1 | CP8 SUPERHEATER SOOTBLOWER 1 MANUAL EXTEND SELECT (SCADA) | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.BURNER.PRIM_DAMPER_STAT | Int | %DB1.DBW154 | CP13 PRIMARY AIR DAMPER STATUS (0 = FAULT, 1 = CLOSED, 2 = OPEN) | Cyclic in operation | 1 s
IDB CP13 FILTER SCREW A.Rem_Cmds.RemoteCtrl | Bool | %DB126.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
IDB CP5 OIL BURNER.Rem_Cmds.RemoteCtrl | Bool | %DB125.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SEND/RECV COOLER 3.SEND.GENERAL.REMOTE_RUN | Bool | %DB163.DBX70.7 | 0 = STOP / 1 = RUN | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.STK_1_PID_MTHD_4_SEL | Bool | %DB1.DBX7.4 | STOKER 1 PID CONTROLLER METHOD 4 SELECTED | Cyclic in operation | 1 s
Warning_Popup3 | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.STOP.TIMERS.DISTRIB_SCREW_1MTR10 | S5Time | %DB30.DBW124 | HOPPER DISTRIBUTION SCREW | Cyclic in operation | 1 s
IDB CP13 PAC AGITATOR.Status.StatusWord | Int | %DB143.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT04.HIHI | Real | %DB41.DBD2400 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.PID.HI_PRESS_CTRL_STEAM.OP_SCALE | Real | %DB40.DBD1564 | OUTPUT SCALE FACTOR (LMN_FAC) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.OP_MODES.OP_MODE_0 | Bool | %DB30.DBX8.0 | SYSTEM IN OPERATION MODE 0 (MANUAL) | Cyclic in operation | 1 s
DB SETPOINTS.PID.RECIRC_FAN.INTEGRAL | Int | %DB40.DBW1324 | I TERM (TI) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4TT01.HYST | Real | %DB41.DBD1904 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD1.CP3_ENMASSE_INLET_BLOCK | Bool | %DB11.DBX105.3 | CP3 EN-MASSE CHAIN CONVEYOR SECOND INLET CHUTE BLOCKED ALARM | Cyclic in operation | 1 s
IDB GR HYD PUMP 2 PBUS.Status.Load | Real | %DB504.DBD42 | Drive Load in Percentage (%) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 3.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_HI | Real | %DB163.DBD186 | CIRCULATION WATER OUTLET TEMPERATURE HIGH ALARM | Cyclic in operation | 1 s
DB SETPOINTS.PID.SECOND_FAN.GAIN | Real | %DB40.DBD1412 | P TERM (GAIN) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_1_SPD_FACTOR | Real | %DB40.DBD472 | GRATE SPEED FACTOR | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.VALVES.CP8_2CV06 | Bool | %DB45.DBX16.3 | CP8 STEAM STOP VALVE 2CV06 SOLENOID | Cyclic in operation | 1 s
DB SETPOINTS.PID.PRIM_FAN.SP | Real | %DB40.DBD1352 | INTERNAL SETPOINT | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2PT03.HIHI | Real | %DB41.DBD2752 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.START.TIMERS.HYD_PWR_PACK_1MTR01 | S5Time | %DB30.DBW84 | HYDRAULIC POWER PACK | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.FEED_WTR_TANK_PRDS_CTRL.PID_ACTV | Bool | %DB42.DBX1560.1 | PID CONTROLLER ACTIVE | Cyclic in operation | 1 s
Shutdown AYS Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.RECIRC_FAN.OUTPUT | Real | %DB42.DBD1668 | OUTPUT VALUE | Cyclic in operation | 1 s
IDB CP3 STOKER HYD PMP 3.Status.StatusWord | Int | %DB114.DBW22 | Motor Status Word | Cyclic in operation | 1 s
IDB CP3 STOKER HYD PMP 1.Status.StatusWord | Int | %DB112.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD4.CP17_4PT02 | Bool | %DB11.DBX15.4 | CP17 FEEDWATER DIFFERENTIAL PRESSURE TRANSMITTER (4-20mA = 6-600 mBar) | Cyclic in operation | 1 s
IDB CP13 FILT SCREW B DP.Status | Int | %DB548.DBW2 | Motor Status | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.BURNER.RECIRC_DAMPER_TIMEOUT | Int | %DB40.DBW962 | RECIRCULATION AIR DAMPER TIMEOUT TIME (SEC) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_3EM01.LOLO | Real | %DB41.DBD2956 | LOW LOW ALARM SETPOINT | Cyclic in operation | 1 s
IDB CP3 STOKER HYD PMP 3.Rem_Cmds.RunFwd | Bool | %DB114.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.START.TIMERS.BICARB_SYS | S5Time | %DB30.DBW156 | SODIUM BICARBONATE SILO AND FEED SYSTEM | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP7_7TT06.HYST | Real | %DB41.DBD656 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BURNER.BRN_TEMP_1TT04_IN_USE | Bool | %DB1.DBX36.7 | RESIDANCE CHAMBER TEMPERATURE PROBE 1TT04 VALUE IN USE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TSZ03.HI | Real | %DB41.DBD2596 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.LOLO.WORD6 | Int | %DB12.DBW74 | LOW LOW ALARMS - WORD 6 | Continuous | 1 s
DB SEND/RECV COOLER 4.RECV.PROCESS_VALUES.CIRC_WATER_OUT_TEMP | Real | %DB164.DBD22 | CIRCULATION WATER OUTLET TEMPERATURE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP7_7TT07.HI | Real | %DB41.DBD612 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_3PI01a.HYST | Real | %DB41.DBD976 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB ALARMS.REMOTE.WORD1.CP13d_A23_TRP | Bool | %DB11.DBX83.1 | CP13d 3MTR12a DUTY ALMIG BELT 22 AIR COMPRESSOR 1 TRIP | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.BOILER_1_MD | Bool | %DB1.DBX18.6 | CP8 BOILER SOOTBLOWER 1 MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
4PU01_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_PID_FLOW_OUT_3 | Real | %DB40.DBD100 | STOKER PID AIR FLOW OUTPUT 3 | Cyclic in operation | 1 s
IDB SCND AIR FAN PBUS.Recv.StatusWord | Word | %DB514.DBW24 | Status Word | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_SB1b | Bool | %DB45.DBX21.2 | CP13 RACK 4 FILTER 1 INLET VALVE B CLOSED | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.OP_MODES.OP_MODE_5 | Bool | %DB30.DBX8.5 | SYSTEM IN OPERATION MODE 5 (RUNNING) | Cyclic in operation | 1 s
DB MV TURB POWER METER.M6_PAC3200.V2_V3 | Real | %DB202.DBD16 | VOLTS PHASE 2 TO PHASE 3 (VOLTS) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_PID_FLOW_2 | Real | %DB40.DBD284 | STOKER PID AIR FLOW POINT 2 | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK5.ALARM103 | Bool | %DB400.DBX236.7 | MECHANICAL TRIP | Cyclic in operation | 1 s
3VAS02_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_PUMP.RAMP_RATE | Real | %DB40.DBD1862 | RAMP TO SETPOINT RATE | Cyclic in operation | 1 s
DB LV GRID POWER METER.M4_PAC3200.V1_N | Real | %DB200.DBD0 | VOLTS PHASE 1 TO NEUTRAL (VOLTS) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.LOLO.WORD4.CP17_4LC02 | Bool | %DB11.DBX71.1 | CP17 DEAERATOR WATER LEVEL TRANSDUCER (4-20mA = 0-100%) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2LT01.HYST | Real | %DB41.DBD2672 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB SEND/RECV COOLER 1.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_HIHI | Real | %DB161.DBD182 | CIRCULATION WATER OUTLET TEMPERATURE HIGH HIGH ALARM | Cyclic in operation | 1 s
DB PROCESS VALUES.EMISSIONS.CO_Mg_m3 | Real | %DB42.DBD804 | CARBON MONOXIDE CO (Mg/m3) | Continuous | 1 s
DB MV TURB POWER METER.KVAtot | Real | %DB202.DBD152 | TOTAL APPARANT POWER (KVA) | Cyclic in operation | 1 s
DB SETPOINTS.PID.BICARB_FEED_HCL.OP_SCALE | Real | %DB40.DBD2116 | OUTPUT SCALE FACTOR (LMN_FAC) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.BURNER.CP18_K951 | Bool | %DB45.DBX14.1 | CP18 MOVING GRATE 1 FORWARD SOLENOID 1CV17 (UPPER RIGHT) | Cyclic in operation | 1 s
IDB CP13 ID FAN A.Rem_Cmds.RunFwd | Bool | %DB131.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
S7_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SAFETY.RECV.OS13d_ESPB_OK | Bool | %DB44.DBX3.0 | BICARB LOADING STATION OS13d EM STOP P/BUTTON HEALTHY (1=HEALTHY) | Cyclic in operation | 1 s
IDB CP13 RECIRC AIR FAN.Status.StatusWord | Int | %DB145.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_PID_FAN_SPD_OUT_4 | Real | %DB40.DBD272 | STOKER PID AIR FAN SPEED OUTPUT 4 | Cyclic in operation | 1 s
4CV05_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.FEED_WTR_TANK_TEMP_CTRL.RAMP_ACTV | Bool | %DB42.DBX1920.0 | RAMP ACTIVE | Cyclic in operation | 1 s
DB SETPOINTS.PID.SECOND_FAN.RAMP_RATE | Real | %DB40.DBD1402 | RAMP TO SETPOINT RATE | Cyclic in operation | 1 s
IDB CP6 WATER TREATMENT.Status.StatusWord | Int | %DB189.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB SETPOINTS.PID.BICARB_FEED.SP | Real | %DB40.DBD1766 | INTERNAL SETPOINT | Cyclic in operation | 1 s
IDB CP7 MN FEED PUMP.Rem_Cmds.RunFwd | Bool | %DB180.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB SEND/RECV COOLER 6.RECV.ADIABATIC.STATUS | Int | %DB166.DBW30 | ADIABATIC SYSTEM STATUS | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD2.CP13R4_U113_DP | Bool | %DB11.DBX11.3 | CP13 RACK 4 FILTER 1 DIFFERENTIAL PRESSURE | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.TURBINE.POWER | Real | %DB42.DBD1116 | TURBINE POWER | Cyclic in operation | 1 s
STOKER_PMP_SHOW | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.PID.BOILER_FEED_WATER_VLV.OP_SCALE | Real | %DB40.DBD1242 | OUTPUT SCALE FACTOR (LMN_FAC) | Cyclic in operation | 1 s
IDB CP2 HYD PUMP HTR.Rem_Cmds.RunFwd | Bool | %DB102.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_8LT04.HIHI | Real | %DB41.DBD1632 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_2_PID_FLOW_OUT_4 | Real | %DB40.DBD520 | GRATE PID AIR FLOW OUTPUT 4 | Cyclic in operation | 1 s
DB SETPOINTS.PID.TEMP_CTRL_STEAM_OUT.OP_SCALE | Real | %DB40.DBD1610 | OUTPUT SCALE FACTOR (LMN_FAC) | Cyclic in operation | 1 s
IDB CP3 SCR CHN SLID VLV.Status.StatusWord | Int | %DB105.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.BICARB_FEED.PID_ACTV | Bool | %DB42.DBX1950.1 | PID CONTROLLER ACTIVE | Cyclic in operation | 1 s
DB SEND/RECV COOLER 5.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_LO | Real | %DB165.DBD190 | CIRCULATION WATER OUTLET TEMPERATURE LOW ALARM | Cyclic in operation | 1 s
DB SETPOINTS.PID.STOKER_1.CYCLE_TIME | Int | %DB40.DBW1452 | SAMPLE TIME (CYCLE) | Cyclic in operation | 1 s
STRT UREA SKID | Timer | %T114 | UREA DeNOx SKID START DELAY TIMER | Cyclic in operation | 1 s
DB SEND/RECV COOLER 4.SEND.GENERAL.REMOTE_AUTO | Bool | %DB164.DBX70.6 | 0 = REMOTE MANUAL / 1 = REMOTE AUTO | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_TEMP_CTRL.OP_MAX | Real | %DB40.DBD1740 | OUTPUT MAX VALUE (LMN_HLM) | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.BURNER.MODE9_HOURS | Real | %DB42.DBD1252 | BURNER MODE 9 COUNTDOWN TIME - HOURS | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.EMISSIONS.WID_LIMIT_SP_MINS | Int | %DB40.DBW930 | SETPOINT FOR WOOD FEED SUSPENSION DUE TO WID LIMIT EXCEEDED (MINS) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.STOP.TIMERS.EN_MASSE_CHN_1MTR09 | S5Time | %DB30.DBW122 | EN-MASSE CHAIN CONVEYOR | Cyclic in operation | 1 s
DB MV TURB POWER METER.M6_PAC3200.V1_N | Real | %DB202.DBD0 | VOLTS PHASE 1 TO NEUTRAL (VOLTS) | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK2.GEN_COOLING_TEMP | DInt | %DB400.DBD92 | GEN. COOLING TEMPERATURE DEG C (x100) | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK3.BEARING_TEMP_9 | DInt | %DB400.DBD132 | TURBINE BEARING TEMPERATURE POS 84.9 DEG C (x100) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.PUSH_FLOOR.CP2_OBSTR_PRESET | Real | %DB40.DBD0 | PUSH FLOOR OBSTRUCTION ALARM COUNTER PRESET | Cyclic in operation | 1 s
DB SEND/RECV COOLER 4.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_HI | Real | %DB164.DBD186 | CIRCULATION WATER OUTLET TEMPERATURE HIGH ALARM | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK2.BEARING_TEMP_3 | DInt | %DB400.DBD108 | TURBINE BEARING TEMPERATURE POS 84.3 DEG C (x100) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MAIN_CTRL.AUTORUN_AVAIL | Bool | %DB30.DBX0.0 | SYSTEM AUTO START AVAILABLE | Cyclic in operation | 1 s
DB SCADA DATA.DWORD_DATA.SD_CHLORINE_IN | Real | %DB45.DBD108 | CHLORINE CONTENT FROM SULPHUR DOSING PLANT | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FEED_LINE.CP18_K941 | Bool | %DB45.DBX7.3 | CP18 STOKER 2 REVERSE RUN RELAY | Cyclic in operation | 1 s
CP8 SOOTB CYC HOLD | Bool | %M88.5 | CP8 CONDITIONS TO HOLD SOOTHING CYCLE | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.OIL_BURNER_CUTOFF_TEMP | Real | %DB40.DBD416 | RESIDENCE CHAMBER AUX BURNER DISABLE TEMPERATURE (DEG C) | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_PUMP.OP_OFFSET | Real | %DB40.DBD1890 | OUTPUT OFFSET (LMN_OFF) | Cyclic in operation | 1 s
DB SETPOINTS.PID.BICARB_FEED_HCL.SP | Real | %DB40.DBD2088 | INTERNAL SETPOINT | Cyclic in operation | 1 s
IDB CP13 PRIM AIR FAN.Rem_Cmds.RemoteCtrl | Bool | %DB146.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MODE_NB.EXEC_MODE_REQ | Int | %DB30.DBW24 | EXECUTIVE OVERRIDE OPERTION MODE NUMBER REQUESTED | Cyclic in operation | 1 s
1MTR10_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SEND/RECV COOLER 4.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_LO | Real | %DB164.DBD190 | CIRCULATION WATER OUTLET TEMPERATURE LOW ALARM | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.BURNER.BURN_PRESS_TRIP | Int | %DB40.DBW940 | COMBUSTION CHAMBER VACUUM (PRESSURE) TRIP FAULT THRESHOLD TIME (SEC) | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.FEED_PUMP.CURR_SP | Real | %DB42.DBD2012 | CURRENT RAMP SETPOINT | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK2.U_WIND_TEMP | DInt | %DB400.DBD68 | WINDING TEMPERATURE U DEG C (x100) | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_5 | Bool | %DB2.DBX294.4 | Profibus Node | Cyclic in operation | 1 s
IDB GR HYD PUMP 1 PBUS.Status.ErrorCode | Int | %DB503.DBW46 | Last Trip Code | Cyclic in operation | 1 s
DB SETPOINTS.PID.RECIRC_FAN.RAMP_RATE | Real | %DB40.DBD1310 | RAMP TO SETPOINT RATE | Cyclic in operation | 1 s
IDB CP8 ECONOM SOOTBLO 2.Status.StatusWord | Int | %DB122.DBW22 | Motor Status Word | Cyclic in operation | 1 s
IDB CP7 SB FEED PUMP.Rem_Cmds.RunFwd | Bool | %DB181.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.WOOD_FEED.STK_1_PID_SEL_PV | Int | %DB1.DBW174 | CP3 STOKER 1 FEED PID (0 = STANDARD, 1 = LAMBDA, 2 = FAN SPEED, 3 = AIR FLOW) | Cyclic in operation | 1 s
STOP 1GR01 | Timer | %T44 | CP22 EDDY CURRENT SEPARATOR STOP DELAY TIMER | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_PID_FLOW_OUT_3 | Real | %DB40.DBD308 | STOKER PID AIR FLOW OUTPUT 3 | Cyclic in operation | 1 s
1MTR04_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_3EM01.HIHI | Real | %DB41.DBD2944 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FEED_LINE.CP18_1SW11 | Bool | %DB45.DBX7.1 | CP18 STOKER 1 REVERSE PROXIMITY SWITCH | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_39 | Bool | %DB2.DBX298.6 | Profibus Node | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_SPD_MIN | Real | %DB40.DBD132 | STOKER MINIMUM SPEED | Cyclic in operation | 1 s
DB SETPOINTS.PID.OIL_BURNER.MAN_AUTO | Bool | %DB40.DBX1710.0 | PID MANUAL/AUTO MODE (1=MANUAL) (MAN_ON) | Cyclic in operation | 1 s
DB SETPOINTS.PID.PRESS_CTRL_STEAM_OUT.OP_MAX | Real | %DB40.DBD1648 | OUTPUT MAX VALUE (LMN_HLM) | Cyclic in operation | 1 s
IDB CP7 LIFT PUMP 2.Rem_Cmds.RemoteCtrl | Bool | %DB183.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.RC_WOOD_BURN_TEMP | Real | %DB40.DBD404 | RESIDENCE CHAMBER MIN TEMPERATURE FOR WOOD BURNING (DEG C) | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.SOOTBLOWERS.SHEAT_2_NB_1 | Int | %DB40.DBW1014 | SUPERHEATER SOOTBLOWER 2 NUMBER 1 | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TT01.LOLO | Real | %DB41.DBD3020 | LOW LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2LT01.HI | Real | %DB41.DBD2660 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
IDB CP7 LIFT PUMP 2.Status.StatusWord | Int | %DB183.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2PSZ02.HYST | Real | %DB41.DBD2800 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB SETPOINTS.PID.RECIRC_FAN.MANUAL_VAL | Real | %DB40.DBD1316 | PID OUTPUT IN MANUAL (MAN) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.START.BITS.EN_MASSE_CHN_1MTR09 | Bool | %DB30.DBX74.0 | EN-MASSE CHAIN CONVEYOR | Cyclic in operation | 1 s
IDB GR HYD PUMP 2 PBUS.Control.RefSpeed | Real | %DB504.DBD32 | Drive Speed Reference in Percentage (%) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT02.HIHI | Real | %DB41.DBD2336 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BOILER.CP7_PLANT_PUMP_START_SP | Real | %DB40.DBD640 | TREATED WATER TANK WATER PRESSURE TO START PLANT PUMP SETPOINT (Bar) | Cyclic in operation | 1 s
8MTR03_SO2_PID_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.PID.HI_TEMP_CTRL_STEAM.GAIN | Real | %DB40.DBD1504 | P TERM (GAIN) | Cyclic in operation | 1 s
IDB CP8 ECONOM SOOTBLO 3.Status.StatusWord | Int | %DB123.DBW22 | Motor Status Word | Cyclic in operation | 1 s
3HP01_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
IDB CP12 TURBINE COOL DP.Load | Real | %DB537.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.OP_MODES.OP_MODE_6 | Bool | %DB30.DBX8.6 | SYSTEM IN OPERATION MODE 6 (TICK-OVER) | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.TURBINE.GEN_OUT_TEMP | Real | %DB42.DBD1136 | GENERATOR OUTLET TEMPERATURE | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP19_2TT01 | Real | %DB42.DBD376 | CP19 TEMPERATURE BEFORE DESUPERHEATER (TC) (???-??? ºC) | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.FILTER.FILT1_IN_VLV_STAT | Int | %DB1.DBW222 | FILTER 1 INLET VALVE STATUS | Cyclic in operation | 1 s
CP2 PUSH FLR AT REV | Bool | %M54.6 | CP2 PUSH FLOOR FULLY REVERSE DETECTED | Cyclic in operation | 1 s
DB SETPOINTS.PID.SECOND_FAN.DERIVATIVE | Time | %DB40.DBD1436 | <No Value> | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD6.CP19_2CV02_POS | Bool | %DB11.DBX19.0 | CP19 SUPERHEATER BLOW OUT VALVE ACTUAL POSITION | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MODE_STATUS.EXEC_OPMODE_8_STAT | Int | %DB30.DBW48 | EXECUTIVE OVERRIDE MODE 8 STATUS (0=NOT SEL, 1=REQ, 2=REQ & ACHIEVED) | Cyclic in operation | 1 s
IDB ID FAN A PBUS.Status.Load | Real | %DB511.DBD50 | Drive Load in Percentage (%) | Cyclic in operation | 1 s
IDB CP3 STOKER HYD PMP 3.Status.Running | Bool | %DB114.DBX20.7 | Motor Running | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.START.BITS.UREA_SKID | Bool | %DB30.DBX148.4 | UREA DeNOx SKID | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.LOLO.WORD7 | Int | %DB12.DBW76 | LOW LOW ALARMS - WORD 7 | Continuous | 1 s
8MTR06_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ESTOPS.WORD2 | Int | %DB12.DBW80 | EMERGENCY STOP ALARMS - WORD 2 | Continuous | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD3.CP13R4_8IN02 | Bool | %DB11.DBX12.6 | CP13 RACK 4 RESIDUE SILO HEPA FILTER PRESSURE | Cyclic in operation | 1 s
DB SAFETY.SEND.GRID_SUPPLY_ON | Bool | %DB44.DBX81.0 | Main Switch Closed | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP7_U75 | Real | %DB42.DBD72 | CP7 BOILER TOTAL DISOLVED SOLIDS CONDUCTIVITY (4-20mA = 0-9990uS/cm) | Cyclic in operation | 1 s
IDB CP13 ID FAN A.Status.StatusWord | Int | %DB131.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_PUMP.INTEGRAL | Int | %DB40.DBW1876 | I TERM (TI) | Cyclic in operation | 1 s
DB SETPOINTS.PID.HI_PRESS_CTRL_STEAM.INTEGRAL | Int | %DB40.DBW1554 | I TERM (TI) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_PID_FLOW_1 | Real | %DB40.DBD72 | STOKER PID AIR FLOW POINT 1 | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_PID_LAMBDA_MIN | Real | %DB40.DBD116 | STOKER PID AIR LAMBDA MINIMUM SCALING VALUE | Cyclic in operation | 1 s
DB SETPOINTS.PID.BOILER_FEED_WATER_VLV.MANUAL_VAL | Real | %DB40.DBD1224 | PID OUTPUT IN MANUAL (MAN) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4FT01.HI | Real | %DB41.DBD1956 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.STOP.TIMERS.FILTER_PLANT | S5Time | %DB30.DBW192 | BAG FILTER PLANT AND PULSE CONTROLLERS | Cyclic in operation | 1 s
3SL01_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP2_1TS06.HYST | Real | %DB41.DBD80 | ALARM HISTERESYS | Cyclic in operation | 1 s
IDB REC AIR FAN PBUS.Status.ErrorCode | Int | %DB515.DBW54 | Last Trip Code | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.PUSH_FLOOR.CP2_K94 | Bool | %DB45.DBX4.1 | CP2 PUSH FLOOR FORWARD RUN RELAY | Cyclic in operation | 1 s
Stoker3PID_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.PUSH_FLOOR.STATUS | Int | %DB1.DBW108 | CP2 PUSH FLOOR SOLENOIDS STATUS (SCADA DISPLAY) | Cyclic in operation | 1 s
DB LV GEN POWER METER.M5_PAC3200.V1_N | Real | %DB201.DBD0 | VOLTS PHASE 1 TO NEUTRAL (VOLTS) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BURNER.O2_PURGE_MD | Bool | %DB1.DBX38.7 | O2 METER PURGE MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
ALARMS OK | Bool | %M30.1 | SYSTEM ALARMS HEALTHY | Cyclic in operation | 1 s
DB SETPOINTS.PID.PRESS_CTRL_STEAM_OUT.CYCLE_TIME | Int | %DB40.DBW1636 | SAMPLE TIME (CYCLE) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD6.CP19_2LT01 | Bool | %DB11.DBX18.3 | CP19 DP CELL WATER LEVEL | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP17_4PT01 | Real | %DB42.DBD216 | CP17 DEAERATOR PRESSURE TRANSDUCER (4-20mA = xx Bar) | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK5.ALARM102 | Bool | %DB400.DBX236.6 | MECHANICAL ALARM | Cyclic in operation | 1 s
ID FAN VENTIL MD | Bool | %M106.1 | ID FANS IN VENTILATION MODE | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.LEV_AUG_I_THRESHOLD | Real | %DB40.DBD16 | LEVELLING AUGER OVERCURRENT THRESHOLD (% LOAD) | Cyclic in operation | 1 s
IDB ST HYD PUMP 1 PBUS.Status.ActualSpeed | Real | %DB500.DBD38 | Actual Speed in Percentage (%) | Cyclic in operation | 1 s
STOP 1HP01 | Timer | %T40 | CP2 PUSH FLOOR TRAVEL SOLENOIDS STOP DELAY TIMER | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.ENMASS_CONV_ROT_SENS_OFF | Bool | %DB1.DBX4.2 | CP3 EN-MASSE CHAIN CONVEYOR ROTATION SENSOR DISABLE (SCADA) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_3TI01a.HYST | Real | %DB41.DBD1008 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB SEND/RECV COOLER 2.SEND.TIMES.ADIABATIC_MIN_RUN_TIME | Time | %DB162.DBD218 | COOLER ADIABATIC SYSTEM MINIMUM RUN TIME | Cyclic in operation | 1 s
DB SCADA DATA.DWORD_DATA.SD_BOILER_OUTPUT | Real | %DB45.DBD104 | BOILER OUTPUT FOR SULPHUR DOSING PLANT | Cyclic in operation | 1 s
S11_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SEND/RECV COOLER 1.SEND.GENERAL.REMOTE_AUTO | Bool | %DB161.DBX70.6 | 0 = REMOTE MANUAL / 1 = REMOTE AUTO | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.LO.WORD4.CP17_8LT04 | Bool | %DB11.DBX56.3 | CP17 TREATED WATER TANK LEVEL TRANSDUCER (4-20mA = 0-100%) | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD2.STK_2_JAMMED | Bool | %DB11.DBX106.5 | CP3 STOKER 2 JAMMED ALARM | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.FILTER.BS_VIB_STAT | Int | %DB1.DBW244 | BICARB SILO VIBRATOR STATUS | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_3TI01c.HI | Real | %DB41.DBD1124 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.ID_FAN.RAMP_ACTV | Bool | %DB42.DBX1620.0 | RAMP ACTIVE | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R3_3MTR07_FWD | Bool | %DB45.DBX20.0 | CP13 RACK 3 RESIDUE SILO TANKER LOADING BELLOWS RUN FORWARD | Cyclic in operation | 1 s
IDB CP13 ID FAN B.Status.StatusWord | Int | %DB132.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TSZ01.HI | Real | %DB41.DBD2628 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
1MTR17_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.PID.STOKER_1.OP_MIN | Real | %DB40.DBD1468 | OUTPUT MIN VALUE (LMN_LLM) | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.RECIRC_FAN.CURR_SP | Real | %DB42.DBD1652 | CURRENT RAMP SETPOINT | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK2.BEARING_TEMP_A | DInt | %DB400.DBD84 | GENERATOR BEARING TEMPERATURE A DEG C (x100) | Cyclic in operation | 1 s
DB ALARMS.COOLERS.COOLER5.WORD2.COMMS_FAULT | Bool | %DB11.DBX148.0 | COMMUNICATION FAULT | Cyclic in operation | 1 s
IDB CP7 LIFT PUMP 1.Rem_Cmds.RunFwd | Bool | %DB182.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_3PI01a.HI | Real | %DB41.DBD964 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.WOOD_FEED.STK_2_TRAV_MIN_TIMEOUT | Int | %DB40.DBW908 | STOKER 2 TRAVERSE MINIMUM TIMEOUT TIME (SEC) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.STOP.TIMERS.UREA_SKID | S5Time | %DB30.DBW186 | UREA DeNOx SKID | Cyclic in operation | 1 s
WID_Cnt_Reset_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.FILTER.RC_BICARB_TEMP | Real | %DB40.DBD692 | RESIDENCE CHAMBER MIN TEMPERATURE FOR SODIUM BICARB INJECTION (DEG C) | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.FEED_PUMP.OUTPUT | Real | %DB42.DBD2028 | OUTPUT VALUE | Cyclic in operation | 1 s
IDB CP7 PLANT PUMP 1.Rem_Cmds.RunFwd | Bool | %DB187.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB SEND/RECV COOLER 6.SEND.GENERAL.REMOTE_AUTO | Bool | %DB166.DBX70.6 | 0 = REMOTE MANUAL / 1 = REMOTE AUTO | Cyclic in operation | 1 s
DB SEND/RECV COOLER 5.RECV.GENERAL.FANS_STATUS | Int | %DB165.DBW4 | COOLER FANS STATUS | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.LOLO.WORD4.CP17_8LT04 | Bool | %DB11.DBX70.3 | CP17 TREATED WATER TANK LEVEL TRANSDUCER (4-20mA = 0-100%) | Cyclic in operation | 1 s
Warning_Popup4 | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
2MTR01_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
IDB CP3 GRATE HYD PMP 2.Status.StatusWord | Int | %DB116.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK5.ALARM20 | Bool | %DB400.DBX226.4 | TURBINE N>0 | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4PT01.LOLO | Real | %DB41.DBD1740 | LOW LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.STOP.BITS.HYD_PWR_PACK_1MTR01 | Bool | %DB30.DBX110.3 | HYDRAULIC POWER PACK | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.BURNER.CP18_1SW43 | Bool | %DB45.DBX14.5 | CP18 GRATE 1 REVERSE SWITCH 2 | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.OPN_SHT.WORD7 | Int | %DB12.DBW20 | OPEN/SHORT CIRCUIT ALARMS - WORD 7 | Continuous | 1 s
DB SEND/RECV COOLER 5.RECV.GENERAL.WATCHDOG | Bool | %DB165.DBX0.0 | <No Value> | Cyclic in operation | 1 s
WARNING ACTIVE | Bool | %M30.3 | SYSTEM WARNING ACTIVE | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_PID_FLOW_OUT_2 | Real | %DB40.DBD304 | STOKER PID AIR FLOW OUTPUT 2 | Cyclic in operation | 1 s
8CV01_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.PID.HI_TEMP_CTRL_STEAM.OP_MAX | Real | %DB40.DBD1510 | OUTPUT MAX VALUE (LMN_HLM) | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_TEMP_CTRL.CYCLE_TIME | Int | %DB40.DBW1728 | SAMPLE TIME (CYCLE) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_1_PID_FLOW_2 | Real | %DB40.DBD432 | GRATE PID AIR FLOW POINT 2 | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.EQUIP_STATUS.RC_TEMP_ABV_WOOD_TEMP | Bool | %DB30.DBX13.6 | RESIDENCE CHAMBER IS ABOVE WOOD BURNING TEMPERATURE | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.WOOD_FEED.STOKER_SPRINKLER_STAT | Int | %DB1.DBW184 | STOKER SPRINKLER STATUS (0 = FAULT, 1 = CLOSED, 2 = OPEN) | Cyclic in operation | 1 s
DB ALARMS.COOLERS.COOLER3.WORD2.COMMS_FAULT | Bool | %DB11.DBX140.0 | COMMUNICATION FAULT | Cyclic in operation | 1 s
DB SAFETY.RECV.E13c_K445_ON | Bool | %DB44.DBX5.4 | RECIRC AIR FAN DAMPER 3Vas06b ISOLATION CONTACTOR (0=ISOLATED) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 5.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_HYST | Real | %DB165.DBD198 | CIRCULATION WATER OUTLET TEMPERATURE ALARM HYSTERESIS | Cyclic in operation | 1 s
S10_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
IDB CP8 SPRHEAT SOOTBL 2.Status.StatusWord | Int | %DB118.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.PUSH_FLOOR.CP2_1SW33_MIN | Bool | %DB45.DBX3.1 | CP2 PUSH FLOOR LADDER No 4 MINIMUM PROXIMITY | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD4.CP17_4PT01 | Bool | %DB11.DBX14.6 | CP17 DEAERATOR PRESSURE TRANSDUCER (4-20mA = xx Bar) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD5.CP18_1TT05 | Bool | %DB11.DBX16.4 | CP18 STOKER TEMPERATURE PROBE 1 | Cyclic in operation | 1 s
CP7 8PU01 SELECTED | Bool | %M146.1 | CP7 MAIN LIFT PUMP DUTY SELECTED | Cyclic in operation | 1 s
DB ALARMS TO SCADA.REMOTE.WORD2 | Int | %DB12.DBW84 | REMOTE ALARMS - WORD 2 | Continuous | 1 s
DB ALARMS.PROCESS.WORD1.CP2_SCR_CHN_FST_BLOCK | Bool | %DB11.DBX105.0 | CP2 SCRAPER CHAIN CONVEYOR FIRST DISCHARGE BLOCKED ALARM | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP2_1TS05 | Real | %DB42.DBD4 | CP2 LEVELLING AUGER MOTOR THERMISTOR (PT100 = 0-150 ºC) | Cyclic in operation | 1 s
UreaPID_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.START.TIMERS.SCRAP_CHN_CONV_1MTR03 | S5Time | %DB30.DBW82 | SCRAPER CHAIN CONVEYOR | Cyclic in operation | 1 s
IDB GR HYD PUMP 1 PBUS.Control.RefSpeed | Real | %DB503.DBD32 | Drive Speed Reference in Percentage (%) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 4.RECV.PROCESS_VALUES.COOL_FAN_ACT_SPD | Real | %DB164.DBD26 | COOLING FANS ACTUAL SPEED | Cyclic in operation | 1 s
IDB CP2 HYD PUMP.Status.StatusWord | Int | %DB100.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_PID_FLOW_5 | Real | %DB40.DBD88 | STOKER PID AIR FLOW POINT 5 | Cyclic in operation | 1 s
IDB ST HYD PUMP 3 PBUS.Send.ControlWord | Word | %DB502.DBW8 | Control Word | Cyclic in operation | 1 s
DB SETPOINTS.PID.TURBINE_STEAM_BLEED.MANUAL_VAL | Real | %DB40.DBD1914 | PID OUTPUT IN MANUAL (MAN) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_2TT06.HYST | Real | %DB41.DBD2064 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2SW14 | Bool | %DB45.DBX13.3 | CP8 ECONOMISER SOOTBLOWER 3 EXTENDED PROXIMITY SWITCH | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_38 | Bool | %DB2.DBX298.5 | Profibus Node | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD5.CP18_1TT04 | Bool | %DB11.DBX17.3 | CP18 RESIDENCE CHAMBER TEMPERATURE PROBE 3 | Cyclic in operation | 1 s
DB SETPOINTS.PID.OIL_BURNER.MANUAL_VAL | Real | %DB40.DBD1684 | PID OUTPUT IN MANUAL (MAN) | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.LO.WORD5 | Int | %DB12.DBW58 | LOW ALARMS - WORD 5 | Continuous | 1 s
DB LV GEN POWER METER.KW3 | Real | %DB201.DBD136 | ACTIVE POWER PHASE 3 (KW) | Cyclic in operation | 1 s
IDB CP5 OIL BURNER.Rem_Cmds.RunFwd | Bool | %DB125.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
IDB CP13 FILT DISCH FAN.Rem_Cmds.RunFwd | Bool | %DB130.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
IDB PLC.PLC.LEDs.BUS2F | Bool | %DB2.DBX52.5 | CPU Interface BUS 2 (PROFINET) Fault Status | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_1TT11.HYST | Real | %DB41.DBD1456 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP7_7TT08 | Real | %DB42.DBD88 | CP7 AMBIENT TEMPERATURE (4-20mA = 0-150 ºC) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_8LT04.LOLO | Real | %DB41.DBD1644 | LOW LOW ALARM SETPOINT | Cyclic in operation | 1 s
IDB CP13 RECIRC AIR FAN.Rem_Cmds.RemoteCtrl | Bool | %DB145.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
IDB CP7 HP DOSING PUMP.Status.StatusWord | Int | %DB184.DBW22 | Motor Status Word | Cyclic in operation | 1 s
CP7 PP AUTO C_OVER OCC | Bool | %M152.3 | CP7 PLANT WATER PUMP AUTO CHANGEOVER OCCURED | Cyclic in operation | 1 s
DB EMISSIONS DATA.WID_ALARM_COUNT_M | Int | %DB300.DBW172 | WID ALARM COUNTER MINUTES | Cyclic in operation | 1 s
FEED1_SHOW | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD5.CP18_1TT09 | Bool | %DB11.DBX17.6 | CP18 SECONDARY AIR DUCT AIR TEMPERATURE PROBE | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.WOOD_FEED.STK_2_TRAV_MAX_TIMEOUT | Int | %DB40.DBW886 | STOKER 2 TRAVERSE MAXIMUM TIMEOUT TIME (SEC) | Cyclic in operation | 1 s
DB SAFETY.RECV.EN_2CV02 | Bool | %DB44.DBX9.1 | SAFETY ENABLE 2CV02 BLOWOUT VALVE (1=OK) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 4.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_HYST | Real | %DB164.DBD198 | CIRCULATION WATER OUTLET TEMPERATURE ALARM HYSTERESIS | Cyclic in operation | 1 s
Stoker2Curves_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.HIHI.WORD4.CP17_4LC02 | Bool | %DB11.DBX29.1 | CP17 DEAERATOR WATER LEVEL TRANSDUCER (4-20mA = 0-100%) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.SECOND_AIR_FAN.O2_PID_O2_SP_5 | Real | %DB40.DBD768 | SECONDARY AIR FAN PID CONTROLLER O2 SETPOINT 5 | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_3TI01d.HI | Real | %DB41.DBD1156 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_PID_FAN_SPD_OUT_2 | Real | %DB40.DBD160 | STOKER PID AIR FAN SPEED OUTPUT 2 | Cyclic in operation | 1 s
DB SAFETY.RECV.CP19_3EM01 | Bool | %DB44.DBX5.1 | BOILER PANEL CP19 LO COMBUSTION CHAMBER OXYGEN LEVEL TRIP (1=HEALTHY) | Cyclic in operation | 1 s
DB ALARMS TO SCADA.SUPPLIES.WORD3 | Int | %DB12.DBW90 | POWER SUPPLY ALARMS - WORD 3 | Continuous | 1 s
DB ALARMS TO SCADA.ANALOGUE.HIHI.WORD4 | Int | %DB12.DBW28 | HIGH HIGH ALARMS - WORD 4 | Continuous | 1 s
DB PROCESS VALUES.MISCELLANEOUS.TURBINE_2.VOLT_L2_L3 | Real | %DB42.DBD1416 | VOLTAGE L2-L3 | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_1_PID_FLOW_1 | Real | %DB40.DBD428 | GRATE PID AIR FLOW POINT 1 | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FEED_LINE.CP18_1SW10 | Bool | %DB45.DBX7.0 | CP18 STOKER 1 FORWARD PROXIMITY SWITCH | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FEED_LINE.CP18_K93 | Bool | %DB45.DBX7.6 | CP18 STOKER 3 FORWARD RUN RELAY | Cyclic in operation | 1 s
IDB CP2 SCRAPER CHAIN DP.Load | Real | %DB522.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
IDB CP7 MN FEED PUMP.Rem_Cmds.RemoteCtrl | Bool | %DB180.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.BURNER.RECIRC_DAMPER_STAT | Int | %DB1.DBW156 | CP13 RECIRCULATION AIR DAMPER STATUS (0 = FAULT, 1 = CLOSED, 2 = OPEN) | Cyclic in operation | 1 s
IDB FEED PUMP 2 PBUS.Control.RefSpeed | Real | %DB509.DBD32 | Drive Speed Reference in Percentage (%) | Cyclic in operation | 1 s
DB SAFETY.RECV.CP19_2TSZ01 | Bool | %DB44.DBX4.4 | BOILER PANEL CP19 HI HI STEAM OUTLET TEMP GUARD TRIP (1=HEALTHY) | Cyclic in operation | 1 s
DB LV GEN POWER METER.M5_PAC3200.I2 | Real | %DB201.DBD28 | CURRENT PHASE 2 (AMPS) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2SW10 | Bool | %DB45.DBX12.3 | CP8 ECONOMISER SOOTBLOWER 1 EXTENDED PROXIMITY SWITCH | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.FEED_WTR_TANK_TEMP_CTRL.PID_ACTV | Bool | %DB42.DBX1920.1 | PID CONTROLLER ACTIVE | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.MAINS.CP1_K261_ON | Bool | %DB45.DBX0.5 | CP1 MAINS A.C.B. CLOSED (GRID) (1=ON) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_1FT02.HYST | Real | %DB41.DBD1360 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_2_SPD_MIN | Real | %DB40.DBD540 | GRATE MINIMUM SPEED | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.FILTER.FILT2_OUT_GT_IN_ALM | Int | %DB40.DBW990 | FILTER 2 OUTLET TEMPERATURE GREATER THAN INLET TEMPERATURE ALARM TIME (SEC) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.SECOND_AIR_FAN.O2_PID_LOAD_3 | Real | %DB40.DBD740 | SECONDARY AIR FAN PID CONTROLLER LOAD POINT 3 | Cyclic in operation | 1 s
DB MV TURB POWER METER.KWh | Real | %DB202.DBD164 | ACTIVE ENERGY USAGE (KWh) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 5.SEND.TIMES.ADIABATIC_MIN_RUN_TIME | Time | %DB165.DBD218 | COOLER ADIABATIC SYSTEM MINIMUM RUN TIME | Cyclic in operation | 1 s
IDB CP13 RS INCL SCR DP.Load | Real | %DB559.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
DB LV GRID POWER METER.M4_PAC3200.I2 | Real | %DB200.DBD28 | CURRENT PHASE 2 (AMPS) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT05.HI | Real | %DB41.DBD2180 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD1.CP2_LEV_AUG_OI_DET | Bool | %DB11.DBX104.6 | CP2 LEVELLING AUGER OVERCURRENT DETECTION ALARM | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_PID_FLOW_3 | Real | %DB40.DBD80 | STOKER PID AIR FLOW POINT 3 | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK5.ALARM124 | Bool | %DB400.DBX239.4 | OIL MIST SEPARATOR ON | Cyclic in operation | 1 s
IDB CP13 FILTER 1 HEATER.Status.StatusWord | Int | %DB135.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.OP_MODES.OP_MODE_7 | Bool | %DB30.DBX8.7 | SYSTEM IN OPERATION MODE 7 (SHUTDOWN 1 - PURGE) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2PT01.HIHI | Real | %DB41.DBD2688 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
4CV03_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
IDB PRIM AIR FAN PBUS.Status.ActualSpeed | Real | %DB513.DBD46 | Actual Speed in Percentage (%) | Cyclic in operation | 1 s
IDB CP13 PAC FEED SCR DP.Load | Real | %DB556.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.FILTER.RES_SILO_BELLOWS_RAISE | Bool | %DB1.DBX29.7 | RESIDUE SILO BELLOWS MANUAL RAISE SELECT (SCADA) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2PT05.HI | Real | %DB41.DBD2916 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.START.TIMERS.PUSH_FLOOR_1HP01 | S5Time | %DB30.DBW88 | PUSH FLOOR TRAVEL SOLENOIDS | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BOILER.BLOWDOWN_COOL_VLV_OPN | Bool | %DB1.DBX22.6 | CP19 BLOWDOWN VESSEL WATER COOLING VALVE MANUAL OPEN SELECT (SCADA) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.SOOTBLOWERS.START_SOOTBLOW_TEMP_STRT | Real | %DB40.DBD712 | TEMPERATURE SETPOINT TO START SOOTBLOWERS | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.SOOTBLOWERS.START_SOOTBLOW_FLOW_SP | Real | %DB40.DBD724 | FLOW SETPOINT TO START SOOTBLOWERS | Cyclic in operation | 1 s
CP1 M6 PAC3200 RX OK | Bool | %M200.2 | CP1 DATA RECEIVED OK FROM M6 MV TURBINE POWER METER | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_U112_DP.HI | Real | %DB41.DBD836 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
IDB CP13 FILT DISCH FAN.Rem_Cmds.RemoteCtrl | Bool | %DB130.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.FILTER.DIF_PRESS_STRT_VENT | Real | %DB40.DBD696 | DIFFERENTIAL PRESSURE TO START VENT FILTER | Cyclic in operation | 1 s
CP7 8PU01/02 SELECT | Bool | %M146.0 | CP7 LIFT PUMP DUTY REQUEST (SCADA) (0=MAIN. 1=STANDBY) | Cyclic in operation | 1 s
GRATE_PMP_SHOW | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_2_PID_FLOW_1 | Real | %DB40.DBD488 | GRATE PID AIR FLOW POINT 1 | Cyclic in operation | 1 s
S12_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.STOKER_1.OUTPUT | Real | %DB42.DBD1758 | OUTPUT VALUE | Cyclic in operation | 1 s
ILocks Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
IDB CP3 STOKER HYD PMP 2.Status.Running | Bool | %DB113.DBX20.7 | Motor Running | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP17_8LT01 | Real | %DB42.DBD200 | CP17 PLANT WATER TANK LEVEL TRANSDUCER (4-20mA = 0-100%) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT02.HI | Real | %DB41.DBD2340 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_11 | Bool | %DB2.DBX295.2 | Profibus Node | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD1.CP3_ENMASSE_CHAIN_ROT | Bool | %DB11.DBX105.6 | CP3 EN-MASSE CHAIN CONVEYOR ROTATION FAULT | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_TEMP_CTRL.OP_MIN | Real | %DB40.DBD1744 | OUTPUT MIN VALUE (LMN_LLM) | Cyclic in operation | 1 s
DB SETPOINTS.PID.SECOND_FAN.SP | Real | %DB40.DBD1398 | INTERNAL SETPOINT | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP19_2CV01_POS | Real | %DB42.DBD360 | CP19 SUPERHEATER 2 STEAM OUTLET VALVE ACTUAL POSITION (4-20mA=???) | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.BURNER.GRT_1_TRAV_INTERVAL | Int | %DB40.DBW950 | GRATE 1 TRAVERSE INTERVAL TIME (SEC) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_S2541 | Bool | %DB45.DBX20.2 | CP13 RACK 4 RESIDUE SILO LOADING BELLOWS SLACK ROPE PROXIMITY | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.HIHI.WORD6.CP19_2PT01 | Bool | %DB11.DBX32.4 | CP19 STEAM DRUM PRESSURE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_1FT03.HIHI | Real | %DB41.DBD1408 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
IDB CP7 HP DOSING PUMP.Rem_Cmds.RunFwd | Bool | %DB184.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP19_2PT01 | Real | %DB42.DBD336 | CP19 STEAM DRUM PRESSURE (4-20mA = 0-63 Bar) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.SLIDE_VLV_OPN | Bool | %DB1.DBX4.6 | CP3 SLIDE VALVE MANUAL OPEN SELECT (SCADA) | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.WOOD_FEED.STOKER_RUNON_TIME_MODE7 | Int | %DB40.DBW892 | STOKER RUN-ON TIME IN AUTO MODE 7 - PURGE (MIN) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_PID_FLOW_OUT_2 | Real | %DB40.DBD200 | STOKER PID AIR FLOW OUTPUT 2 | Cyclic in operation | 1 s
IDB CP13 BS BLOW SEAL.Rem_Cmds.RemoteCtrl | Bool | %DB142.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_TEMP_CTRL.GAIN | Real | %DB40.DBD1734 | P TERM (GAIN) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.MAINS.CP1_VC6_P17 | Bool | %DB45.DBX0.6 | CP1 TURBINE 11KV MV SWITCH CLOSED (1=ON) | Cyclic in operation | 1 s
DB LV GRID POWER METER.KWtot | Real | %DB200.DBD156 | TOTAL ACTIVE POWER (KW) | Cyclic in operation | 1 s
IDB CP3 EN-MASSE CHN DP.Status | Int | %DB530.DBW2 | Motor Status | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.CP8_SOOTB_1_INSERV | Bool | %DB1.DBX21.0 | CP8 SOOTBLOWER 1 IN SERVICE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_2PT06.HYST | Real | %DB41.DBD1712 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BOILER.DEAERATOR_OVERFL_VLV_OPN | Bool | %DB1.DBX23.3 | CP17 DEAERATOR OVERFLOW VALVE MANUAL OPEN SELECT (SCADA) | Cyclic in operation | 1 s
DB SAFETY.RECV.EN_2CV06 | Bool | %DB44.DBX9.2 | SAFETY ENABLE 2CV06 SOOTBLOWER STOP VALVE (1=OK) | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.LOLO.WORD5 | Int | %DB12.DBW72 | LOW LOW ALARMS - WORD 5 | Continuous | 1 s
STOP UREA SKID | Timer | %T101 | UREA DeNOx SKID STOP DELAY TIMER | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.FILTER.BS_MAINT_VLV_MD | Bool | %DB1.DBX31.4 | BICARB SILO MAINTENANCE BUTTERFLY VALVE MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
BS_PULSE VLV ACTIVE | Bool | %M118.2 | BICARB SILO PULSE VALVE ACTIVE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_1FT02.LO | Real | %DB41.DBD1352 | LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BURNER.GRATE_1_MAN_MD | Bool | %DB1.DBX37.0 | CP3 GRATE 1 TRAVERSE MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2MTR02_FWD | Bool | %DB45.DBX10.4 | CP8 SUPERHEATER SOOTBLOWER 2 MOTOR RUN FORWARD | Cyclic in operation | 1 s
DB SETPOINTS.PID.PRESS_CTRL_STEAM_OUT.MANUAL_VAL | Real | %DB40.DBD1638 | PID OUTPUT IN MANUAL (MAN) | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.BOILER_FEED_WATER_VLV.PID_ACTV | Bool | %DB42.DBX1590.1 | PID CONTROLLER ACTIVE | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.PUSH_FLOOR.CP2_LAD_5_INSERV | Bool | %DB1.DBX3.0 | CP2 PUSH FLOOR LADDER 5 IN SERVICE | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD6.CP19_2TT01 | Bool | %DB11.DBX19.6 | CP19 TEMPERATURE BEFORE DESUPERHEATER | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FEED_LINE.CP18_K921 | Bool | %DB45.DBX6.7 | CP18 STOKER 1 REVERSE RUN RELAY | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_PID_FLOW_OUT_4 | Real | %DB40.DBD208 | STOKER PID AIR FLOW OUTPUT 4 | Cyclic in operation | 1 s
1MTR14_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_PRDS_CTRL.RAMP_EN | Bool | %DB40.DBX1204.2 | RAMP ENABLED (1=ENABLED) | Cyclic in operation | 1 s
IDB CP13 FILTER 2 HEATER.Rem_Cmds.RunFwd | Bool | %DB136.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
IDB CP8 BOILER SOOTBLO 2.Status.StatusWord | Int | %DB120.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD6.CP17_5CV01_TIMEOUT | Bool | %DB11.DBX115.1 | CP17 TURBINE STEAM BLEED TO DEAERATOR VALVE TIMEOUT ALARM | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK5.ALARM101 | Bool | %DB400.DBX236.5 | COMMON TRIP | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.ID_FAN.OUTPUT | Real | %DB42.DBD1638 | OUTPUT VALUE | Cyclic in operation | 1 s
DB LV GEN POWER METER.KVA1 | Real | %DB201.DBD116 | APPARANT POWER PHASE 1 (KVA) | Cyclic in operation | 1 s
WtrTreat_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.PID.HI_TEMP_CTRL_STEAM.INTEGRAL | Int | %DB40.DBW1508 | I TERM (TI) | Cyclic in operation | 1 s
DB SETPOINTS.PID.OIL_BURNER.OP_SCALE | Real | %DB40.DBD1702 | OUTPUT SCALE FACTOR (LMN_FAC) | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_PUMP.MAN_AUTO | Bool | %DB40.DBX1894.0 | PID MANUAL/AUTO MODE (1=MANUAL) (MAN_ON) | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP19_2TSZ03 | Real | %DB42.DBD324 | CP19 TEMPERATURE SWITCH AFTER SUPERHEATER 2 (4-20mA = 0-450 ºC) | Cyclic in operation | 1 s
Ash_Load_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SAFETY.RECV.CP_RH_ESPB_OK | Bool | %DB44.DBX3.2 | CONTROL ROOM R/HAND EM STOP P/BUTTON HEALTHY (1=HEALTHY) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD6.CP19_2CV01_POS | Bool | %DB11.DBX19.2 | CP19 SUPERHEATER 2 STEAM OUTLET VALVE ACTUAL POSITION | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP13R4_3TI01b | Real | %DB42.DBD128 | CP13 RACK 4 FILTER 1 OUTLET AIR TEMPERATURE (4..20mA = -50 - +300ºC) | Cyclic in operation | 1 s
IDB GR HYD PUMP 1 PBUS.Status.ActualSpeed | Real | %DB503.DBD38 | Actual Speed in Percentage (%) | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.WOOD_FEED.STK_3_STATUS | Int | %DB1.DBW172 | CP3 STOKER 3 SOLENOIDS STATUS (SCADA DISPLAY) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT01.HIHI | Real | %DB41.DBD2304 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SAFETY.RECV.CP3_ESPB_OK | Bool | %DB44.DBX2.4 | BURNER PANEL CP3 EM STOP P/BUTTON HEALTHY (1=HEALTHY) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.BURNER.CP18_1SW45 | Bool | %DB45.DBX15.1 | CP18 GRATE 2 REVERSE SWITCH 1 | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4TT01.HIHI | Real | %DB41.DBD1888 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT03.HI | Real | %DB41.DBD2372 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.SOOTBLOWERS.START_SOOTBLOW_PRESS_SP | Real | %DB40.DBD716 | PRESSURE SETPOINT TO START SOOTBLOWERS | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_1_PID_FLOW_OUT_3 | Real | %DB40.DBD456 | GRATE PID AIR FLOW OUTPUT 3 | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.BURNER.GRATE_TIMER_REMAIN | Int | %DB1.DBW144 | GRATES RUN-ON TIMER REMAINING TIME (MODE 8) | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP19_2TSZ01 | Real | %DB42.DBD328 | CP19 TEMPERATURE GUARD STEAM OUTLET SUPERHEATER 2 (4-20mA = 0-450 ºC) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_8PT01.HI | Real | %DB41.DBD1668 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
IDB SCND AIR FAN PBUS.Send.ControlWord | Word | %DB514.DBW8 | Control Word | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_PID_FLOW_1 | Real | %DB40.DBD176 | STOKER PID AIR FLOW POINT 1 | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_2_SPD_FACTOR | Real | %DB40.DBD532 | GRATE SPEED FACTOR | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD2.CP13R4_3TI01a | Bool | %DB11.DBX11.7 | CP13 RACK 4 FILTER 1 INLET AIR TEMPERATURE | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BURNER.BRN_VAC_1PT02_IN_USE | Bool | %DB1.DBX36.2 | BURNER BACKUP VACUUM SENSOR 1PT02 IN SERVICE | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.WOOD_FEED.LEV_AUG_OVERI_TIME | Int | %DB40.DBW878 | LEVELLING AUGER OVERCURRENT RESUME TIME (SEC) | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_42 | Bool | %DB2.DBX299.1 | Profibus Node | Cyclic in operation | 1 s
IDB CP13 RS HORIZ SCREW.Rem_Cmds.RemoteCtrl | Bool | %DB134.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SAFETY.SEND.FWP1_4PU01_RUNNING | Bool | %DB44.DBX81.1 | 4PU01 Feed Water Pump No 1 Running (1=Running) | Cyclic in operation | 1 s
DB ALARMS.REMOTE.WORD1.CP13d_A24_TRP | Bool | %DB11.DBX83.3 | CP13d 3MTR12b DUTY ALMIG BELT 22 AIR COMPRESSOR 2 TRIP | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP7_7TT07 | Real | %DB42.DBD76 | CP7 COOLING CIRCULATION WATER FLOW TEMPERATURE (4-20mA = 0-150 ºC) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD3.CP13R4_3TI01d | Bool | %DB11.DBX12.4 | CP13 RACK 4 FILTER 2 OUTLET AIR TEMPERATURE | Cyclic in operation | 1 s
DB SETPOINTS.PID.RECIRC_FAN.OP_MAX | Real | %DB40.DBD1326 | OUTPUT MAX VALUE (LMN_HLM) | Cyclic in operation | 1 s
STRT 1HP01 | Timer | %T56 | CP2 PUSH FLOOR TRAVEL SOLENOIDS START DELAY TIMER | Cyclic in operation | 1 s
DB SETPOINTS.PID.BICARB_FEED.OP_MIN | Real | %DB40.DBD1790 | OUTPUT MIN VALUE (LMN_LLM) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.START.BITS.SCRAP_CHN_CONV_1MTR03 | Bool | %DB30.DBX74.3 | SCRAPER CHAIN CONVEYOR | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD5.CP18_1TT01 | Bool | %DB11.DBX17.0 | CP18 MOVING GRATE TEMPERATURE | Cyclic in operation | 1 s
DB MV TURB POWER METER.KVArh | Real | %DB202.DBD168 | REACTIVE ENERGY USAGE (KVArh) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_PID_FLOW_OUT_2 | Real | %DB40.DBD96 | STOKER PID AIR FLOW OUTPUT 2 | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_3TI01d.HIHI | Real | %DB41.DBD1152 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.BOILER.CP7_U33_MAN_OVR | Bool | %DB45.DBX28.1 | CP7 STANDBY BOILER FEED PUMP IN MANUAL OVERRIDE MODE | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_PID_FAN_SPD_OUT_1 | Real | %DB40.DBD156 | STOKER PID AIR FAN SPEED OUTPUT 1 | Cyclic in operation | 1 s
DB ALARMS TO SCADA.PANEL_TEMP.WORD1 | Int | %DB12.DBW102 | PANEL TEMPERATURE ALARMS - WORD 1 | Continuous | 1 s
IDB CP13 FILTER 1 HEATER.Rem_Cmds.RunFwd | Bool | %DB135.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_PID_LAMBDA_MIN | Real | %DB40.DBD324 | STOKER PID AIR LAMBDA MINIMUM SCALING VALUE | Cyclic in operation | 1 s
CP7 4PU01 SELECTED | Bool | %M142.1 | CP7 MAIN BOILER FEED PUMP DUTY SELECTED | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2SW03 | Bool | %DB45.DBX10.6 | CP8 SUPERHEATER SOOTBLOWER 2 RETRACTED PROXIMITY SWITCH | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_PID_FLOW_OUT_3 | Real | %DB40.DBD204 | STOKER PID AIR FLOW OUTPUT 3 | Cyclic in operation | 1 s
STOP ASH SYS | Timer | %T105 | ASH CONVEYING AND STORAGE SYSTEM STOP DELAY TIMER | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_PID_FAN_SPD_2 | Real | %DB40.DBD36 | STOKER PID AIR FAN SPEED POINT 2 | Cyclic in operation | 1 s
DB SETPOINTS.PID.SECOND_FAN.MANUAL_VAL | Real | %DB40.DBD1408 | PID OUTPUT IN MANUAL (MAN) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.BURNER.CP18_K961 | Bool | %DB45.DBX14.7 | CP18 MOVING GRATE 2 FORWARD SOLENOID 1CV19 (LOWER RIGHT) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BOILER.STEAM_STOP_VLV_MD | Bool | %DB1.DBX22.3 | CP8 STEAM STOP VALVE MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.OIL_BURNER.OUTPUT | Real | %DB42.DBD1908 | OUTPUT VALUE | Cyclic in operation | 1 s
DB SETPOINTS.PID.OIL_BURNER.SP | Real | %DB40.DBD1674 | INTERNAL SETPOINT | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.FILTER.BS_PULSE_CTRL_STAT | Int | %DB1.DBW236 | BICARB SILO PULSE CONTROLLER STATUS | Cyclic in operation | 1 s
DB SETPOINTS.PID.PRIM_FAN.MAN_AUTO | Bool | %DB40.DBX1388.0 | PID MANUAL/AUTO MODE (1=MANUAL) (MAN_ON) | Cyclic in operation | 1 s
DB SETPOINTS.PID.RECIRC_FAN.CYCLE_TIME | Int | %DB40.DBW1314 | SAMPLE TIME (CYCLE) | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.BURNER.BRN_TEMP_SENS_VALUE | Real | %DB42.DBD1280 | BURNER COMBUSTION ZONE TEMPERATURE SENSOR VALUE | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.HI_TEMP_CTRL_STEAM.PID_ACTV | Bool | %DB42.DBX1770.1 | PID CONTROLLER ACTIVE | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK1.WATER_INJ_VALVE_POS | DInt | %DB400.DBD40 | WATER INJECTION VALVE OPENING POSITION % | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD2.CP13R4_3LO01 | Bool | %DB11.DBX11.4 | CP13 RACK 4 RESIDUE SILO LOAD CELL WEIGHT | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD3.CP13R4_1TT11 | Bool | %DB11.DBX13.5 | CP13 RACK 4 SECONDARY AIR TEMPERATURE | Cyclic in operation | 1 s
DB SETPOINTS.PID.PRESS_CTRL_STEAM_OUT.GAIN | Real | %DB40.DBD1642 | P TERM (GAIN) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1PT02.HIHI | Real | %DB41.DBD2464 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP7_7TT07.LO | Real | %DB41.DBD616 | LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB MV TURB POWER METER.KW1 | Real | %DB202.DBD128 | ACTIVE POWER PHASE 1 (KW) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.STOKER_2_MAN_ST | Bool | %DB1.DBX5.5 | CP3 STOKER 2 TRAVERSE MANUAL START SELECT (SCADA) | Cyclic in operation | 1 s
O2_Purge_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.FILTER.SCREW_1_ON_TIME | Int | %DB40.DBW996 | FILTER DISCHARGE SCREW 1 ON TIME | Cyclic in operation | 1 s
DB EMISSIONS DATA.BURNING_WOOD_OIL | Int | %DB300.DBW166 | BURNING WHAT? (0=NOT BURNING, 1=OIL, 2=WOOD) | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD2.STK_1_JAMMED | Bool | %DB11.DBX106.2 | CP3 STOKER 1 JAMMED ALARM | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP17_4LC02 | Real | %DB42.DBD228 | CP17 DEAERATOR WATER LEVEL TRANSDUCER (4-20mA = 0-100%) | Cyclic in operation | 1 s
IDB CP13 SECON AIR FAN.Status.StatusWord | Int | %DB147.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.SULPHUR_DOS_EN | Bool | %DB1.DBX7.5 | CP21 SULPHUR DOSING SYSTEM ENABLE/DISABLE SELECT (SCADA) | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP19_2TT02 | Real | %DB42.DBD380 | CP19 TEMPERATURE AFTER DESUPERHEATER (TC) (???-??? ºC) | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.HIHI.WORD1 | Int | %DB12.DBW22 | HIGH HIGH ALARMS - WORD 1 | Continuous | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP18_1TT07 | Real | %DB42.DBD280 | CP18 MOVING GRATE TEMPERATURE PROBE (0-400 ºC) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.SOOTHING_STOP | Bool | %DB1.DBX20.7 | CP8 SOOTHING CYCLE MANUAL STOP SELECT (SCADA) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT02.HYST | Real | %DB41.DBD2352 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB SEND/RECV COOLER 3.RECV.PROCESS_VALUES.CIRC_WATER_OUT_TEMP | Real | %DB163.DBD22 | CIRCULATION WATER OUTLET TEMPERATURE | Cyclic in operation | 1 s
IDB CP3 SLIDE VLV DP.Status | Int | %DB533.DBW2 | Motor Status | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R3_3MTR07_REV | Bool | %DB45.DBX20.1 | CP13 RACK 3 RESIDUE SILO TANKER LOADING BELLOWS RUN REVERSE | Cyclic in operation | 1 s
1MTR01_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_PRDS_CTRL.CYCLE_TIME | Int | %DB40.DBW1176 | SAMPLE TIME (CYCLE) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT06.HI | Real | %DB41.DBD2212 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_1TT11.HIHI | Real | %DB41.DBD1440 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
3MTR03_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.LO.WORD2 | Int | %DB12.DBW52 | LOW ALARMS - WORD 2 | Continuous | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.STOKER_SPRINKLER_OPN | Bool | %DB1.DBX7.0 | CP3 STOKER SPRINKLER MANUAL OPEN SELECT (SCADA) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.HIHI.WORD6.CP19_2LT01 | Bool | %DB11.DBX32.3 | CP19 DP CELL WATER LEVEL | Cyclic in operation | 1 s
IDB CP6 WATER TREATMENT.Rem_Cmds.RunFwd | Bool | %DB189.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_S246 | Bool | %DB45.DBX22.7 | CP13 RACK 4 RESIDUE SILO TOP ENTRY LEVEL PROBE | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MODE_STATUS.EXEC_OPMODE_4_STAT | Int | %DB30.DBW40 | EXECUTIVE OVERRIDE MODE 4 STATUS (0=NOT SEL, 1=REQ, 2=REQ & ACHIEVED) | Cyclic in operation | 1 s
MODE 6 Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FEED_LINE.CP18_1LS03 | Bool | %DB45.DBX6.5 | CP18 STOKER LEVEL SENSOR 2 | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.PRIM_FAN.OUTPUT | Real | %DB42.DBD1698 | OUTPUT VALUE | Cyclic in operation | 1 s
User Name | WString | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.PUSH_FLOOR.CP2_1SW32_MIN | Bool | %DB45.DBX2.7 | CP2 PUSH FLOOR LADDER No 3 MINIMUM PROXIMITY | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_K274 | Bool | %DB45.DBX21.6 | CP13 RACK 4 RESIDUE SILO MAINTENANCE BUTTERFLY VALVE OPEN SOLENOID 3VAS02 | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.TURBINE.OIL_COOL_RUNON_TIME | Int | %DB40.DBW918 | TURBINE AND ALTERNATOR OIL COOLERS RUN-ON TIME (MIN) | Cyclic in operation | 1 s
IDB CP13 ID FAN B.Rem_Cmds.RemoteCtrl | Bool | %DB132.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_2_PID_FLOW_OUT_5 | Real | %DB40.DBD524 | GRATE PID AIR FLOW OUTPUT 5 | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_1TT10.HIHI | Real | %DB41.DBD1376 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.SOOTHING_START | Bool | %DB1.DBX20.6 | CP8 SOOTHING CYCLE MANUAL START SELECT (SCADA) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.ECONOM_1_MD | Bool | %DB1.DBX19.4 | CP8 ECONOMISER SOOTBLOWER 1 MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
DB SETPOINTS.PID.RECIRC_FAN.OP_SCALE | Real | %DB40.DBD1334 | OUTPUT SCALE FACTOR (LMN_FAC) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.STOP.BITS.SCRAP_CHN_CONV_1MTR03 | Bool | %DB30.DBX110.2 | SCRAPER CHAIN CONVEYOR | Cyclic in operation | 1 s
DB SETPOINTS.PID.PRIM_FAN.OP_OFFSET | Real | %DB40.DBD1384 | OUTPUT OFFSET (LMN_OFF) | Cyclic in operation | 1 s
STOP BICARB SYS | Timer | %T102 | SODIUM BICARBONATE SILO AND FEED SYSTEM STOP DELAY TIMER | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.SOOTBLOWERS.ECON_2_NB_1 | Int | %DB40.DBW1022 | ECONOMISER SOOTBLOWER 2 NUMBER 1 | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.BURNER.PRIM_DAMPER_TIMEOUT | Int | %DB40.DBW958 | PRIMARY AIR DAMPER TIMEOUT TIME (SEC) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_PID_FAN_SPD_OUT_1 | Real | %DB40.DBD260 | STOKER PID AIR FAN SPEED OUTPUT 1 | Cyclic in operation | 1 s
DB LV GRID POWER METER.KVA1 | Real | %DB200.DBD116 | APPARANT POWER PHASE 1 (KVA) | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK4.POWER_FACTOR | DInt | %DB400.DBD196 | POWER FACTOR | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2SW05 | Bool | %DB45.DBX11.2 | CP8 BOILER SOOTBLOWER 1 RETRACTED PROXIMITY SWITCH | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK3.OIL_TANK_TEMP | DInt | %DB400.DBD156 | OIL TANK TEMPERATURE DEG C (x100) | Cyclic in operation | 1 s
ALL SAF INST OK | Bool | %M40.1 | ALL SAFETY INSTRUMENTS HEALTHY | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.OPN_SHT.WORD3 | Int | %DB12.DBW12 | OPEN/SHORT CIRCUIT ALARMS - WORD 3 | Continuous | 1 s
DB LV GEN POWER METER.M5_PAC3200.PF2 | Real | %DB201.DBD76 | POWER FACTOR PHASE 2 | Cyclic in operation | 1 s
IDB ID FAN A PBUS.Status.ActualSpeed | Real | %DB511.DBD46 | Actual Speed in Percentage (%) | Cyclic in operation | 1 s
IDB CP13 FILTER 2 HEATER.Rem_Cmds.RemoteCtrl | Bool | %DB136.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.EQUIP_STATUS.OIL_BURNER_IS_OFF | Bool | %DB30.DBX12.1 | OIL BURNER IS OFF | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.PRESS_CTRL_STEAM_OUT.PID_ACTV | Bool | %DB42.DBX1860.1 | PID CONTROLLER ACTIVE | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_PID_FLOW_OUT_5 | Real | %DB40.DBD316 | STOKER PID AIR FLOW OUTPUT 5 | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.MAINS.CP1_Q58_Q_3 | Bool | %DB45.DBX0.0 | CP1 TRANSFORMER RUNNING ON GRID OR DIESEL FROM CP1 (1=DIESEL) | Cyclic in operation | 1 s
DB ALARMS.ESTOPS.WORD2.CP7_2LSZ01 | Bool | %DB11.DBX80.1 | BOILER PANEL CP7 BOILER HI HI WATER LEVEL TRIP | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_1FT02.HI | Real | %DB41.DBD1348 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SEND/RECV COOLER 6.SEND.TIMES.ADIABATIC_MIN_RUN_TIME | Time | %DB166.DBD218 | COOLER ADIABATIC SYSTEM MINIMUM RUN TIME | Cyclic in operation | 1 s
DB SETPOINTS.PID.HI_TEMP_CTRL_STEAM.MANUAL_VAL | Real | %DB40.DBD1500 | PID OUTPUT IN MANUAL (MAN) | Cyclic in operation | 1 s
Stoker1PID_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4PT01.LO | Real | %DB41.DBD1736 | LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB LV GRID POWER METER.M4_PAC3200.PF3 | Real | %DB200.DBD80 | POWER FACTOR PHASE 3 | Cyclic in operation | 1 s
S1_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.PID.BOILER_FEED_WATER_VLV.OP_MAX | Real | %DB40.DBD1234 | OUTPUT MAX VALUE (LMN_HLM) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2PT05.LOLO | Real | %DB41.DBD2924 | LOW LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT04.HYST | Real | %DB41.DBD2416 | ALARM HISTERESYS | Cyclic in operation | 1 s
IDB ID FAN A PBUS.Status.ErrorCode | Int | %DB511.DBW54 | Last Trip Code | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD6.CP19_2PT01 | Bool | %DB11.DBX18.4 | CP19 STEAM DRUM PRESSURE | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.TEMP_CTRL_STEAM_OUT.OUTPUT | Real | %DB42.DBD1848 | OUTPUT VALUE | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.PUSH_FLOOR.CP2_K45 | Bool | %DB45.DBX2.2 | CP2 HYDRAULIC PUMP MOTOR RUNNING | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2LT01.LOLO | Real | %DB41.DBD2668 | LOW LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.TURBINE.WINDING_TEMP_W | Real | %DB42.DBD1148 | WINDING TEMPERATURE W | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK3.NO_OF_STARTS | DInt | %DB400.DBD164 | NUMBER OF STARTS | Cyclic in operation | 1 s
IDB CP13 BS BLOW FAN DP.Load | Real | %DB553.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
IDB CP13 RS LOAD BELL DP.Status | Int | %DB558.DBW2 | Motor Status | Cyclic in operation | 1 s
IDB CP13 FILT SCREW A DP.Status | Int | %DB547.DBW2 | Motor Status | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.WOOD_FEED.WOOD_FEED_START_DEL | Int | %DB40.DBW904 | WOOD FEED START DELAY TIMER (SEC) | Cyclic in operation | 1 s
CP3 CP5 1BU01 RNG | Bool | %I75.1 | CP3 CP5 DUNPHY OIL BURNER RUNNING | Cyclic in operation | 1 s
DB SETPOINTS.PID.ID_FAN.OP_MAX | Real | %DB40.DBD1280 | OUTPUT MAX VALUE (LMN_HLM) | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.RECIRC_FAN.RAMP_ACTV | Bool | %DB42.DBX1650.0 | RAMP ACTIVE | Cyclic in operation | 1 s
DB ALARMS.ESTOPS.WORD2.CP7_2LSZ02_03 | Bool | %DB11.DBX80.0 | BOILER PANEL CP7 BOILER LOW LOW WATER LEVEL TRIP | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD4.CP17_2FT01 | Bool | %DB11.DBX15.7 | CP17 SUPERHEATER 2 FLOW METER STEAM OUTLET | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_1_PID_FLOW_3 | Real | %DB40.DBD436 | GRATE PID AIR FLOW POINT 3 | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP18_1TT08 | Real | %DB42.DBD284 | CP18 PRIMARY AIR DUCT AIR TEMPERATURE PROBE (PT100) (0-400 ºC) | Cyclic in operation | 1 s
IDB ID FAN B PBUS.Status.ErrorCode | Int | %DB512.DBW54 | Last Trip Code | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.STOP.BITS.ASH_SYS | Bool | %DB30.DBX182.5 | ASH CONVEYING AND STORAGE SYSTEM | Cyclic in operation | 1 s
IDB ID FAN A PBUS.Control.RefSpeed | Real | %DB511.DBD40 | Drive Speed Reference in Percentage (%) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.STK_3_PID_MTHD_1_SEL | Bool | %DB1.DBX8.2 | STOKER 3 PID CONTROLLER METHOD 1 SELECTED | Cyclic in operation | 1 s
CP1 M5 PAC3200 RX OK | Bool | %M200.1 | CP1 DATA RECEIVED OK FROM M5 LV GENERATOR POWER METER | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.EQUIP_STATUS.RC_TEMP_BEL_WOOD_TEMP | Bool | %DB30.DBX13.2 | RESIDENCE CHAMBER IS BELOW WOOD BURNING TEMPERATURE | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.STK_1_PID_MTHD_2_SEL | Bool | %DB1.DBX7.2 | STOKER 1 PID CONTROLLER METHOD 2 SELECTED | Cyclic in operation | 1 s
User Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
BICARB_SCREW_SHOW | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB PROCESS VALUES.EMISSIONS.FLOW_m3_hr | Real | %DB42.DBD852 | STACK AIR FLOW (m3/hr) | Continuous | 1 s
DB ALARM SETPOINTS.CP7_7TT06.HI | Real | %DB41.DBD644 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.DAMPERS.CP13R4_S265 | Bool | %DB45.DBX30.1 | CP13 RACK 4 PRIMARY AIR DAMPER OPENED | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.FEED_WTR_TANK_PRDS_CTRL.OUTPUT | Real | %DB42.DBD1578 | OUTPUT VALUE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_2FT01.HI | Real | %DB41.DBD2020 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_8PT01.HYST | Real | %DB41.DBD1680 | ALARM HISTERESYS | Cyclic in operation | 1 s
IDB CP13 PRIM AIR FAN.Status.StatusWord | Int | %DB146.DBW22 | Motor Status Word | Cyclic in operation | 1 s
IDB CP12 ALTERNTR COOLER.Status.StatusWord | Int | %DB173.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB SEND/RECV COOLER 3.RECV.GENERAL.WATCHDOG | Bool | %DB163.DBX0.0 | <No Value> | Cyclic in operation | 1 s
IDB CP3 STOKER HYD PMP 2.Rem_Cmds.RunFwd | Bool | %DB113.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
IDB CP13 PAC AGITATOR DP.Status | Int | %DB555.DBW2 | Motor Status | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_S258 | Bool | %DB45.DBX24.0 | CP13 RACK 4 BICARB SILO SURGE HOPPER FULL LEVEL PROBE | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.OUTPUTS.CP13R4_8UR01_CEMS | Real | %DB42.DBD616 | CP13 RACK 4 DeNOx UREA SKID SYSTEM NOx OUTPUT FROM CEMS (4..20mA) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 4.RECV.GENERAL.PUMP_STATUS | Int | %DB164.DBW2 | COOLER PUMP STATUS | Cyclic in operation | 1 s
DB SEND/RECV COOLER 3.SEND.SETPOINTS.FANS_SPEED_MANUAL | Real | %DB163.DBD110 | FANS SPEED FOR REMOTE MANUAL MODE | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.BURNER.CP18_1SW46 | Bool | %DB45.DBX15.2 | CP18 GRATE 2 FORWARD SWITCH 2 | Cyclic in operation | 1 s
HELP_BUTTON | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_2PT06.HI | Real | %DB41.DBD1700 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK5.ALARM100 | Bool | %DB400.DBX236.4 | COMMON ALARM | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_TEMP_CTRL.SP | Real | %DB40.DBD1720 | INTERNAL SETPOINT | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP13R4_1FT02 | Real | %DB42.DBD168 | CP13 RACK 4 PRIMARY AIR FLOW (4..20mA = 0 to 15000 Nm3/H) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP7_7TT07.HYST | Real | %DB41.DBD624 | ALARM HISTERESYS | Cyclic in operation | 1 s
4CV04_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SEND/RECV COOLER 6.SEND.TIMES.MIN_RUN_TIME | Time | %DB166.DBD214 | COOLER MINIMUM RUN TIME | Cyclic in operation | 1 s
EXEC MODE AYS Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_PUMP.MANUAL_VAL | Real | %DB40.DBD1868 | PID OUTPUT IN MANUAL (MAN) | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK2.BEARING_TEMP_6 | DInt | %DB400.DBD120 | TURBINE BEARING TEMPERATURE POS 84.6 DEG C (x100) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.STK_3_PID_MTHD_4_SEL | Bool | %DB1.DBX8.5 | STOKER 3 PID CONTROLLER METHOD 4 SELECTED | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD1.CP2_PSH_FLR_TIMEOUT_TRIP | Bool | %DB11.DBX104.4 | CP2 PUSH FLOOR TRAVERSE TIMEOUT TRIP | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.FILTER.RES_SILO_BELLOWS_MD | Bool | %DB1.DBX29.5 | RESIDUE SILO BELLOWS MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.CHAIN_CONV_ROT_SENS_OFF | Bool | %DB1.DBX4.1 | CP2 SCRAPER CHAIN CONVEYOR ROTATION SENSOR DISABLE (SCADA) | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK1.PRDS_ACT_POSITION | DInt | %DB400.DBD36 | PRDS VALVE OPENING POSITION % | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_20 | Bool | %DB2.DBX296.3 | Profibus Node | Cyclic in operation | 1 s
DB SETPOINTS.PID.SECOND_FAN.OP_MIN | Real | %DB40.DBD1422 | OUTPUT MIN VALUE (LMN_LLM) | Cyclic in operation | 1 s
STRT FILTER PLANT | Timer | %T112 | MAIN FILTER FANS START DELAY TIMER | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BURNER.BRN_BOTH_VAC_IN_USE | Bool | %DB1.DBX36.0 | BURNER AVERAGE OF BOTH VACUUM SENSORS 1PT01 AND 1PT02 IN SERVICE | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.SOOTBLOWERS.ECON_1_NB_1 | Int | %DB40.DBW1020 | ECONOMISER SOOTBLOWER 1 NUMBER 1 | Cyclic in operation | 1 s
IDB CP13 FILTER 2 HEATER.Status.StatusWord | Int | %DB136.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.ECONOM_1_EXT | Bool | %DB1.DBX19.5 | CP8 ECONOMISER SOOTBLOWER 1 MANUAL EXTEND SELECT (SCADA) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT03.HYST | Real | %DB41.DBD2384 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.TURBINE.FREQ | Real | %DB42.DBD1128 | TURBINE FREQUENCY | Cyclic in operation | 1 s
IDB CP13 RS INCLIN SCREW.Status.StatusWord | Int | %DB133.DBW22 | Motor Status Word | Cyclic in operation | 1 s
3MTR04a_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.PID.RECIRC_FAN.RAMP_EN | Bool | %DB40.DBX1342.2 | RAMP ENABLED (1=ENABLED) | Cyclic in operation | 1 s
DB ALARMS TO SCADA.PROCESS.WORD2 | Int | %DB12.DBW106 | PROCESS ALARMS - WORD 2 | Continuous | 1 s
DB MISCELLANEOUS.BITS.BOILER.STEAM_DRAIN_VLV_MD | Bool | %DB1.DBX22.1 | CP8 STEAM DRAIN VALVE MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.BURNER.BRN_TEMP_AVG_VALUE | Real | %DB42.DBD1284 | BURNER COMBUSTION ZONE TEMPERATURE SENSOR AVERAGED VALUE | Cyclic in operation | 1 s
DB SETPOINTS.PID.OIL_BURNER.INTEGRAL | Int | %DB40.DBW1692 | I TERM (TI) | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.LOLO.WORD1 | Int | %DB12.DBW64 | LOW LOW ALARMS - WORD 1 | Continuous | 1 s
DB SETPOINTS.PID.ID_FAN.CYCLE_TIME | Int | %DB40.DBW1268 | SAMPLE TIME (CYCLE) | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.PUSH_FLOOR.CP2_TRAV_TIMEOUT | Int | %DB40.DBW868 | PUSH FLOOR TRAVERSE TIMEOUT TIME (SEC) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.HIHI.WORD4.CP17_8LT01 | Bool | %DB11.DBX28.2 | CP17 PLANT WATER TANK LEVEL TRANSDUCER (4-20mA = 0-100%) | Cyclic in operation | 1 s
ID FAN NORMAL MD | Bool | %M106.3 | ID FANS IN NORMAL OPERATION MODE | Cyclic in operation | 1 s
Warning_Popup2 | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
IDB CP3 DISTRIB SCREW.Rem_Cmds.RemoteCtrl | Bool | %DB110.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB LV GRID POWER METER.KVArtot | Real | %DB200.DBD160 | TOTAL REACTIVE POWER (KVAr) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.FILTER.BS_PULSE_VLV_MD | Bool | %DB1.DBX31.2 | BICARB SILO HOPPER PULSE VALVE MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD4.CP17_4CV02_POS | Bool | %DB11.DBX14.7 | CP17 FEEDWATER CONTROL VALVE ACTUAL POSITION (4-20mA = 0-100%) | Cyclic in operation | 1 s
DB MV TURB POWER METER.KVA2 | Real | %DB202.DBD120 | APPARANT POWER PHASE 2 (KVA) | Cyclic in operation | 1 s
DB SETPOINTS.PID.PRESS_CTRL_STEAM_OUT.OP_OFFSET | Real | %DB40.DBD1660 | OUTPUT OFFSET (LMN_OFF) | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK2.BEARING_TEMP_4 | DInt | %DB400.DBD112 | TURBINE BEARING TEMPERATURE POS 84.4 DEG C (x100) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.FILTER.FILTER2_IN_VLV_A_MD | Bool | %DB1.DBX29.0 | CP13 FILTER 2 INLET VALVE A MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
IDB REC AIR FAN PBUS.Send.ControlWord | Word | %DB515.DBW8 | Control Word | Cyclic in operation | 1 s
IDB CP13 ID FAN B.Rem_Cmds.RunFwd | Bool | %DB132.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP17_8LT04 | Real | %DB42.DBD204 | CP17 TREATED WATER TANK LEVEL TRANSDUCER (4-20mA = 0-100%) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.STOP.TIMERS.PUSH_FLOOR_1HP01 | S5Time | %DB30.DBW112 | PUSH FLOOR TRAVEL SOLENOIDS | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT05.HIHI | Real | %DB41.DBD2176 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
2CV01_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.PID.RECIRC_FAN.MAN_AUTO | Bool | %DB40.DBX1342.0 | PID MANUAL/AUTO MODE (1=MANUAL) (MAN_ON) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.START.TIMERS.EN_MASSE_CHN_1MTR09 | S5Time | %DB30.DBW76 | EN-MASSE CHAIN CONVEYOR | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.LO.WORD3 | Int | %DB12.DBW54 | LOW ALARMS - WORD 3 | Continuous | 1 s
DB CP12 TURBINE.BLOCK2.BEARING_TEMP_5 | DInt | %DB400.DBD116 | TURBINE BEARING TEMPERATURE POS 84.5 DEG C (x100) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.STOP.TIMERS.ASH_SYS | S5Time | %DB30.DBW194 | ASH CONVEYING AND STORAGE SYSTEM | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2PT03.HI | Real | %DB41.DBD2756 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SEND/RECV COOLER 1.SEND.TIMES.MIN_RUN_TIME | Time | %DB161.DBD214 | COOLER MINIMUM RUN TIME | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP13R4_SPARE1 | Real | %DB42.DBD132 | CP13 RACK 4 RESIDUE SILO VENT FILTER DIFF PRESSURE (4..20mA = 0-999 mmWG) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP12_EXH_PRESS.HI | Real | %DB41.DBD3460 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB MV TURB POWER METER.M6_PAC3200.I3 | Real | %DB202.DBD32 | CURRENT PHASE 3 (AMPS) | Cyclic in operation | 1 s
DB SETPOINTS.PID.STOKER_1.RAMP_RATE | Real | %DB40.DBD1448 | RAMP TO SETPOINT RATE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_3EM01.LO | Real | %DB41.DBD2952 | LOW ALARM SETPOINT | Cyclic in operation | 1 s
IDB PLC.PLC.LEDs.FRCE | Bool | %DB2.DBX52.1 | CPU Force Status | Cyclic in operation | 1 s
IDB CP3 SCR CHN SLID VLV.Status.Running | Bool | %DB105.DBX20.7 | Motor Running | Cyclic in operation | 1 s
DB SETPOINTS.PID.BICARB_FEED_HCL.OP_OFFSET | Real | %DB40.DBD2120 | OUTPUT OFFSET (LMN_OFF) | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK5.ALARM115 | Bool | %DB400.DBX238.3 | OIL HEATER ON | Cyclic in operation | 1 s
FEED PMP OK AUTOSTART | Bool | %M144.0 | FEED PUMPS READY / AVAILABLE FOR SYSTEM AUTO START | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_24 | Bool | %DB2.DBX296.7 | Profibus Node | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD1.CP2_SCR_CHAIN_ROT | Bool | %DB11.DBX104.7 | CP2 SCRAPER CHAIN CONVEYOR ROTATION FAULT | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP17_4PT02 | Real | %DB42.DBD240 | CP17 FEEDWATER DIFFERENTIAL PRESSURE TRANSMITTER (4-20mA = 6-600 mBar) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4PLT03.LO | Real | %DB41.DBD1992 | LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARMS TO SCADA.PROFIBUS.WORD1 | Int | %DB12.DBW2 | PROFIBUS ALARMS - WORD 1 | Continuous | 1 s
IDB CP13 RS HORIZ SCR DP.Status | Int | %DB560.DBW2 | Motor Status | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD2.CP13R4_U112_DP | Bool | %DB11.DBX11.2 | CP13 RACK 4 FILTER 1 DIFFERENTIAL PRESSURE | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FEED_LINE.CP18_K94 | Bool | %DB45.DBX7.2 | CP18 STOKER 2 FORWARD RUN RELAY | Cyclic in operation | 1 s
IDB CP3 GRATE HYD PMP 1.Rem_Cmds.RemoteCtrl | Bool | %DB115.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP17_4PLT03 | Real | %DB42.DBD248 | CP17 FEEDWATER PRESSURE TRANSDUCER (4-20mA = 0-100 Bar) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.SPRHEAT_1_MD | Bool | %DB1.DBX18.0 | CP8 SUPERHEATER SOOTBLOWER 1 MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
DB SETPOINTS.PID.BICARB_FEED.MAN_AUTO | Bool | %DB40.DBX1802.0 | PID MANUAL/AUTO MODE (1=MANUAL) (MAN_ON) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.CP8_SOOTB_4_INSERV | Bool | %DB1.DBX21.3 | CP8 SOOTBLOWER 4 IN SERVICE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1PT02.HI | Real | %DB41.DBD2468 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
IDB CP13 BS FEED SCREW.Status.StatusWord | Int | %DB140.DBW22 | Motor Status Word | Cyclic in operation | 1 s
IDB GR HYD PUMP 2 PBUS.Status.ActualSpeed | Real | %DB504.DBD38 | Actual Speed in Percentage (%) | Cyclic in operation | 1 s
DB SETPOINTS.PID.PRIM_FAN.CYCLE_TIME | Int | %DB40.DBW1360 | SAMPLE TIME (CYCLE) | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.BURNER.COMB_LOAD | Real | %DB42.DBD1304 | COMBUSTION LOAD | Cyclic in operation | 1 s
DB SETPOINTS.PID.TEMP_CTRL_STEAM_OUT.MANUAL_VAL | Real | %DB40.DBD1592 | PID OUTPUT IN MANUAL (MAN) | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_TEMP_CTRL.RAMP_EN | Bool | %DB40.DBX1756.2 | RAMP ENABLED (1=ENABLED) | Cyclic in operation | 1 s
Page_Number | UInt | <No Value> | <No Value> | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.BURNER.GRT_2_STATUS | Int | %DB1.DBW148 | CP3 GRATE 2 SOLENOIDS STATUS (SCADA DISPLAY) | Cyclic in operation | 1 s
IDB CP13 FILTER SEAL A.Status.StatusWord | Int | %DB128.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT06.HYST | Real | %DB41.DBD2224 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_PID_FLOW_1 | Real | %DB40.DBD280 | STOKER PID AIR FLOW POINT 1 | Cyclic in operation | 1 s
IDB CP13 BS AGITATOR DP.Status | Int | %DB552.DBW2 | Motor Status | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MODE_STATUS.EXEC_OPMODE_9_STAT | Int | %DB30.DBW50 | EXECUTIVE OVERRIDE MODE 9 STATUS (0=NOT SEL, 1=REQ, 2=REQ & ACHIEVED) | Cyclic in operation | 1 s
1BU01_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SEND/RECV COOLER 2.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_HI | Real | %DB162.DBD186 | CIRCULATION WATER OUTLET TEMPERATURE HIGH ALARM | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.TURBINE.COND_PMP_1_STAT | Int | %DB1.DBW116 | CONDENSATE PUMP 1 STATUS (0 = FAULT, 1 = STOPPED, 2 = RUNNING) | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK4.MAINS_FREQ | DInt | %DB400.DBD220 | MAINS FREQUENCY | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.FILTER.RES_SILO_ARM_RET | Bool | %DB1.DBX29.4 | RESIDUE SILO ARM MANUAL RETRACT SELECT (SCADA) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 3.SEND.GENERAL.START_COOLER | Bool | %DB163.DBX70.5 | <No Value> | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP2_1TS01.HIHI | Real | %DB41.DBD0 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
11RMC5F_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1PT02.HYST | Real | %DB41.DBD2480 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD2.CP7_7TT08 | Bool | %DB11.DBX10.6 | CP7 AMBIENT TEMPERATURE (4-20mA = 0-150 ºC) | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK5.ALARM104 | Bool | %DB400.DBX237.0 | ELECTRICAL ALARM | Cyclic in operation | 1 s
IDB CP3 SLIDE VLV DP.Load | Real | %DB533.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.STK_2_PID_MTHD_4_SEL | Bool | %DB1.DBX8.1 | STOKER 2 PID CONTROLLER METHOD 4 SELECTED | Cyclic in operation | 1 s
DB SETPOINTS.PID.HI_TEMP_CTRL_STEAM.OP_OFFSET | Real | %DB40.DBD1522 | OUTPUT OFFSET (LMN_OFF) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_1TT11.HI | Real | %DB41.DBD1444 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARMS.REMOTE.WORD1.CP13d_A24_ALM | Bool | %DB11.DBX83.2 | CP13d 3MTR12b DUTY ALMIG BELT 22 AIR COMPRESSOR 2 ALARM | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.TEMP_CTRL_STEAM_OUT.PID_ACTV | Bool | %DB42.DBX1830.1 | PID CONTROLLER ACTIVE | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.STOP.TIMERS.ED_CURR_SEP_1GR01 | S5Time | %DB30.DBW120 | EDDY CURRENT SEPARATOR | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BURNER.BRN_VAC_1PT01_IN_USE | Bool | %DB1.DBX36.1 | BURNER MAIN VACUUM SENSOR 1PT01 IN SERVICE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TT07.HIHI | Real | %DB41.DBD3264 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
IDB CP2 LEV AUGER.Rem_Cmds.RemoteCtrl | Bool | %DB103.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2MTR06_REV | Bool | %DB45.DBX12.5 | CP8 ECONOMISER SOOTBLOWER 2 MOTOR RUN REVERSE | Cyclic in operation | 1 s
DB MV TURB POWER METER.M6_PAC3200.V1_V2 | Real | %DB202.DBD12 | VOLTS PHASE 1 TO PHASE 2 (VOLTS) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD5.CP18_1TT07 | Bool | %DB11.DBX16.6 | CP18 MOVING GRATE TEMPERATURE PROBE | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.STOKER_3_MAN_MD | Bool | %DB1.DBX6.0 | CP3 STOKER 3 TRAVERSE MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
DB LV GEN POWER METER.M5_PAC3200.I3 | Real | %DB201.DBD32 | CURRENT PHASE 3 (AMPS) | Cyclic in operation | 1 s
IDB FEED PUMP 2 PBUS.Recv.StatusWord | Word | %DB509.DBW20 | Status Word | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP19_2CV02_POS | Real | %DB42.DBD352 | CP19 SUPERHEATER BLOW OUT VALVE ACTUAL POSITION (4-20mA = ???) | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.STOKER_1.PID_ACTV | Bool | %DB42.DBX1740.1 | PID CONTROLLER ACTIVE | Cyclic in operation | 1 s
DB LV GEN POWER METER.M5_PAC3200.I1 | Real | %DB201.DBD24 | CURRENT PHASE 1 (AMPS) | Cyclic in operation | 1 s
DB MV TURB POWER METER.M6_PAC3200.HZ | Real | %DB202.DBD84 | FREQUENCY (HZ) | Cyclic in operation | 1 s
DB SAFETY.RECV.CP2_ESPB_OK | Bool | %DB44.DBX2.0 | PUSH FLOOR PANEL CP2 EM STOP P/BUTTON HEALTHY (1=HEALTHY) | Cyclic in operation | 1 s
DB SETPOINTS.PID.STOKER_2.MAN_AUTO | Bool | %DB40.DBX1986.0 | PID MANUAL/AUTO MODE (1=MANUAL) (MAN_ON) | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.SOOTBLOWERS.ECON_3_NB_2 | Int | %DB40.DBW1038 | ECONOMISER SOOTBLOWER 3 NUMBER 2 | Cyclic in operation | 1 s
DB LV GRID POWER METER.KW3 | Real | %DB200.DBD136 | ACTIVE POWER PHASE 3 (KW) | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.HI_PRESS_CTRL_STEAM.OUTPUT | Real | %DB42.DBD1818 | OUTPUT VALUE | Cyclic in operation | 1 s
DB ALARMS TO SCADA.PROCESS.WORD7 | Int | %DB12.DBW116 | PROCESS ALARMS - WORD 7 | Continuous | 1 s
SEC_AIR_FAN_SHOW | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP18_1TT02 | Real | %DB42.DBD292 | CP18 RESIDENCE CHAMBER TEMPERATURE PROBE 1 | Cyclic in operation | 1 s
IDB ID FAN B PBUS.Recv.StatusWord | Word | %DB512.DBW24 | Status Word | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.WOOD_FEED.STK_1_TRAV_INTERVAL | Int | %DB40.DBW880 | STOKER 1 TRAVERSE INTERVAL TIME (SEC) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BICARB_FEED.HCL_START_FEED | Real | %DB40.DBD796 | HCL SETPOINT TO START BICARB FEEDING | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.START.TIMERS.ED_CURR_SEP_1GR01 | S5Time | %DB30.DBW78 | EDDY CURRENT SEPARATOR | Cyclic in operation | 1 s
IDB CP2 HYD PUMP HTR.Rem_Cmds.RemoteCtrl | Bool | %DB102.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.SECOND_AIR_FAN.O2_PID_LOAD_1 | Real | %DB40.DBD732 | SECONDARY AIR FAN PID CONTROLLER LOAD POINT 1 | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_3EM01.HI | Real | %DB41.DBD2948 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_34 | Bool | %DB2.DBX298.1 | Profibus Node | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2PT03.LOLO | Real | %DB41.DBD2764 | LOW LOW ALARM SETPOINT | Cyclic in operation | 1 s
3MTR10_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SEND/RECV COOLER 1.SEND.GENERAL.START_ADIABATIC | Bool | %DB161.DBX71.0 | <No Value> | Cyclic in operation | 1 s
DB LV GRID POWER METER.M4_PAC3200.I1 | Real | %DB200.DBD24 | CURRENT PHASE 1 (AMPS) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_1TT10.HYST | Real | %DB41.DBD1392 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB EMISSIONS DATA.WID_ALARM_COUNT_H | Int | %DB300.DBW174 | WID ALARM COUNTER HOURS | Cyclic in operation | 1 s
DB SETPOINTS.PID.TEMP_CTRL_STEAM_OUT.OP_MAX | Real | %DB40.DBD1602 | OUTPUT MAX VALUE (LMN_HLM) | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD6.CP17_4CV03_TIMEOUT | Bool | %DB11.DBX114.2 | CP17 FEEDWATER TO DESUPERHEATER VALVE TIMEOUT ALARM | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD5.CP18_1TT06 | Bool | %DB11.DBX16.5 | CP18 STOKER TEMPERATURE PROBE 2 | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.STK_2_PID_MTHD_1_SEL | Bool | %DB1.DBX7.6 | STOKER 2 PID CONTROLLER METHOD 1 SELECTED | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4FT01.HIHI | Real | %DB41.DBD1952 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB LV GRID POWER METER.M4_PAC3200.PF1 | Real | %DB200.DBD72 | POWER FACTOR PHASE 1 | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_2_PID_FLOW_4 | Real | %DB40.DBD500 | GRATE PID AIR FLOW POINT 4 | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4PT02.HYST | Real | %DB41.DBD1936 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.ALARMS.STATUS | Int | %DB1.DBW278 | SYSTEM ALARMS STATUS (0 = HEALTHY, 1 = WARNING, 2 = ALARM, 3 = TRIP)) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TT05.HYST | Real | %DB41.DBD3152 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD6.CP19_2PSZ02 | Bool | %DB11.DBX18.7 | CP19 STEAM DRUM PRESSURE SWITCH H | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_SPD_MAX | Real | %DB40.DBD232 | STOKER MAXIMUM SPEED | Cyclic in operation | 1 s
IDB CP13 BS BLOW SEAL.Rem_Cmds.RunFwd | Bool | %DB142.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP17_4CV03_POS | Real | %DB42.DBD224 | CP17 FEEDWATER TO DESUPERHEATER CONTROL VALVE ACTUAL POSITION (4-20mA = 0-100%) | Cyclic in operation | 1 s
CP8 SOOTB CYC OK RUN | Bool | %M88.4 | CP8 CONDITIONS TO RUN SOOTHING CYCLE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_U113_DP.HI | Real | %DB41.DBD868 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.WOOD_FEED.STK_2_STATUS | Int | %DB1.DBW170 | CP3 STOKER 2 SOLENOIDS STATUS (SCADA DISPLAY) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BOILER.CP6_WTR_TREAT_START_SP | Real | %DB40.DBD648 | TREATED WATER TANK WATER LEVEL TO START WATER TREATMENT SETPOINT (%) | Cyclic in operation | 1 s
PAC_Load_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MODE_STATUS.SYS_RUN_STAT | Int | %DB30.DBW52 | SYSTEM RUNNING STATUS INDICATION (0 TO 19) | Cyclic in operation | 1 s
DB SETPOINTS.PID.SECOND_FAN.MAN_AUTO | Bool | %DB40.DBX1434.0 | PID MANUAL/AUTO MODE (1=MANUAL) (MAN_ON) | Cyclic in operation | 1 s
DB SETPOINTS.PID.BICARB_FEED_HCL.CYCLE_TIME | Int | %DB40.DBW2096 | SAMPLE TIME (CYCLE) | Cyclic in operation | 1 s
DB SAFETY.RECV.OS2_1_ESPB_OK | Bool | %DB44.DBX2.1 | PUSH FLOOR STATION OS2.1 EM STOP P/BUTTON HEALTHY (1=HEALTHY) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MAIN_CTRL.GRATES_START | Bool | %DB30.DBX1.6 | START BURNER GRATES (FROM SCADA) | Cyclic in operation | 1 s
IDB CP7 PLANT PUMP 1.Rem_Cmds.RemoteCtrl | Bool | %DB187.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.OPN_SHT.WORD6 | Int | %DB12.DBW18 | OPEN/SHORT CIRCUIT ALARMS - WORD 6 | Continuous | 1 s
DB ALARM SETPOINTS.CP13R4_1FT03.HI | Real | %DB41.DBD1412 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.SOOTBLOWERS.BOILER_1_NB_2 | Int | %DB40.DBW1030 | BOILER SOOTBLOWER 1 NUMBER 2 | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.BURNER.CP18_1SW40 | Bool | %DB45.DBX14.2 | CP18 GRATE 1 FORWARD SWITCH 1 | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_1_PID_FLOW_OUT_2 | Real | %DB40.DBD452 | GRATE PID AIR FLOW OUTPUT 2 | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.RC_OPERATING_TEMP | Real | %DB40.DBD412 | RESIDENCE CHAMBER SETPOINT OPERATING TEMPERATURE (DEG C) | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.OUTPUTS.CP3_CP5_BURNER_LOAD | Real | %DB42.DBD600 | CP3 CP5 OIL BURNER LOAD CONTROL (4-20mA - 0-100%) | Cyclic in operation | 1 s
IDB CP13 PAC FEED SCREW.Rem_Cmds.RemoteCtrl | Bool | %DB144.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD4.CP17_4PLT03 | Bool | %DB11.DBX15.6 | CP17 FEEDWATER PRESSURE TRANSDUCER (4-20mA = 0-100 Bar) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.PUSH_FLOOR.CP2_K95 | Bool | %DB45.DBX4.0 | CP2 PUSH FLOOR REVERSE RUN RELAY | Cyclic in operation | 1 s
DB LV GEN POWER METER.M5_PAC3200.V1_V2 | Real | %DB201.DBD12 | VOLTS PHASE 1 TO PHASE 2 (VOLTS) | Cyclic in operation | 1 s
DB SETPOINTS.PID.STOKER_1.INTEGRAL | Int | %DB40.DBW1462 | I TERM (TI) | Cyclic in operation | 1 s
DB ALARMS TO SCADA.LOCAL_ISOL.WORD3 | Int | %DB12.DBW100 | AC MOTOR LOCAL ISOLATOR ALARMS - WORD 3 | Continuous | 1 s
DB ALARM SETPOINTS.CP19_2PT03.LO | Real | %DB41.DBD2760 | LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB LV GRID POWER METER.KVAr2 | Real | %DB200.DBD144 | REACTIVE POWER PHASE 2 (KVAr) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.SECOND_AIR_FAN.O2_PID_O2_SP_3 | Real | %DB40.DBD760 | SECONDARY AIR FAN PID CONTROLLER O2 SETPOINT 3 | Cyclic in operation | 1 s
IDB CP2 HYD PUMP HTR DP.Load | Real | %DB520.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.EQUIP_STATUS.RC_TEMP_ABV_MOD | Bool | %DB30.DBX13.4 | RESIDENCE CHAMBER IS ABOVE MODULATING TEMPERATURE | Cyclic in operation | 1 s
DB SETPOINTS.PID.PRIM_FAN.INTEGRAL | Int | %DB40.DBW1370 | I TERM (TI) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP2_1TS06.HI | Real | %DB41.DBD68 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TT02.HYST | Real | %DB41.DBD3056 | ALARM HISTERESYS | Cyclic in operation | 1 s
IDB CP3 ASH SCRAPER CONV.Rem_Cmds.RemoteCtrl | Bool | %DB111.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
IDB CP12 ALTERN COOL DP.Status | Int | %DB545.DBW2 | Motor Status | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.FILTER.RS_MAINT_VLV_STAT | Int | %DB1.DBW230 | RESIDUE SILO MAINTENANCE VALVE STATUS | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2PT01.LO | Real | %DB41.DBD2696 | LOW ALARM SETPOINT | Cyclic in operation | 1 s
IDB CP8 ECONOM SOOTBLO 1.Status.StatusWord | Int | %DB121.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.SECOND_AIR_FAN.O2_PID_LOAD_4 | Real | %DB40.DBD744 | SECONDARY AIR FAN PID CONTROLLER LOAD POINT 4 | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.STOKER_1.RAMP_ACTV | Bool | %DB42.DBX1740.0 | RAMP ACTIVE | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.PUSH_FLOOR.CP2_LAD_4_INSERV | Bool | %DB1.DBX2.7 | CP2 PUSH FLOOR LADDER 4 IN SERVICE | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD3.CP13R4_3TI01b | Bool | %DB11.DBX12.0 | CP13 RACK 4 FILTER 1 OUTLET AIR TEMPERATURE | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.HI.WORD7 | Int | %DB12.DBW48 | HIGH ALARMS - WORD 7 | Continuous | 1 s
IDB CP13 FILTER SCREW B.Rem_Cmds.RemoteCtrl | Bool | %DB127.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SEND/RECV COOLER 1.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_HI | Real | %DB161.DBD186 | CIRCULATION WATER OUTLET TEMPERATURE HIGH ALARM | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.START.BITS.LEV_SCREW_1MTR02 | Bool | %DB30.DBX74.5 | LEVELLING SCREW | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FEED_LINE.CP18_1SW13 | Bool | %DB45.DBX7.5 | CP18 STOKER 2 REVERSE PROXIMITY SWITCH | Cyclic in operation | 1 s
DB LV GRID POWER METER.KW2 | Real | %DB200.DBD132 | ACTIVE POWER PHASE 2 (KW) | Cyclic in operation | 1 s
IDB CP21 SULPHUR DOS SYS.Rem_Cmds.RunFwd | Bool | %DB124.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB LV GEN POWER METER.KVA2 | Real | %DB201.DBD120 | APPARANT POWER PHASE 2 (KVA) | Cyclic in operation | 1 s
DB MV TURB POWER METER.KW2 | Real | %DB202.DBD132 | ACTIVE POWER PHASE 2 (KW) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_SPD_MIN | Real | %DB40.DBD236 | STOKER MINIMUM SPEED | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.LOLO.WORD3 | Int | %DB12.DBW68 | LOW LOW ALARMS - WORD 3 | Continuous | 1 s
DB SEND/RECV COOLER 3.SEND.GENERAL.START_ADIABATIC | Bool | %DB163.DBX71.0 | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_PID_LAMBDA_MIN | Real | %DB40.DBD220 | STOKER PID AIR LAMBDA MINIMUM SCALING VALUE | Cyclic in operation | 1 s
IDB CP13 FILT SCREW B DP.Load | Real | %DB548.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
2CV02_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_2_PID_FLOW_OUT_2 | Real | %DB40.DBD512 | GRATE PID AIR FLOW OUTPUT 2 | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_13 | Bool | %DB2.DBX295.4 | Profibus Node | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK2.GENERATOR_VIB | DInt | %DB400.DBD64 | VIBRATION MONITORING AT GENERATOR mm/s (x100) | Cyclic in operation | 1 s
2CV05_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARMS.SUPPLIES.WORD5.ALARM15 | Bool | %DB11.DBX95.6 | CP3 EN-MASSE CHAIN CONVEYOR TENSIONER ALARM | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.TURBINE.WINDING_TEMP_U | Real | %DB42.DBD1140 | WINDING TEMPERATURE U | Cyclic in operation | 1 s
1CV05_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
IDB CP2 HYD PUMP.Rem_Cmds.RunFwd | Bool | %DB100.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_S2531 | Bool | %DB45.DBX21.7 | CP13 RACK 4 RESIDUE SILO MAINTENANCE BUTTERFLY VALVE OPENED | Cyclic in operation | 1 s
DB LV GRID POWER METER.KVArh | Real | %DB200.DBD168 | REACTIVE ENERGY USAGE (KVArh) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_S2552 | Bool | %DB45.DBX22.3 | CP13 RACK 4 BICARB SILO MAINTENANCE BUTTERFLY VALVE CLOSED | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_PRDS_CTRL.OP_MIN | Real | %DB40.DBD1192 | OUTPUT MIN VALUE (LMN_LLM) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.STOP.TIMERS.SCRAP_CHN_CONV_1MTR03 | S5Time | %DB30.DBW116 | SCRAPER CHAIN CONVEYOR | Cyclic in operation | 1 s
DB SEND/RECV COOLER 3.RECV.GENERAL.PUMP_STATUS | Int | %DB163.DBW2 | COOLER PUMP STATUS | Cyclic in operation | 1 s
DB SEND/RECV COOLER 1.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_LO | Real | %DB161.DBD190 | CIRCULATION WATER OUTLET TEMPERATURE LOW ALARM | Cyclic in operation | 1 s
IDB FEED PUMP 1 PBUS.Recv.StatusWord | Word | %DB508.DBW20 | Status Word | Cyclic in operation | 1 s
IDB FEED PUMP 1 PBUS.Status.ActualSpeed | Real | %DB508.DBD38 | Actual Speed in Percentage (%) | Cyclic in operation | 1 s
DB ALARMS TO SCADA.PROCESS.WORD1 | Int | %DB12.DBW104 | PROCESS ALARMS - WORD 1 | Continuous | 1 s
DB SETPOINTS.TIMERS.PUSH_FLOOR.CP2_TRAV_INTERVAL | Int | %DB40.DBW870 | PUSH FLOOR TRAVERSE INTERVAL TIME (SEC) | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.SECOND_FAN.RAMP_ACTV | Bool | %DB42.DBX1710.0 | RAMP ACTIVE | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BOILER.BLOWDOWN_COOL_VLV_MD | Bool | %DB1.DBX22.5 | CP19 BLOWDOWN VESSEL WATER COOLING VALVE MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
S5_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
1MTR02_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.FILTER.BS_HOPPER_NB_PULSES | Int | %DB1.DBW218 | BICARB SILO HOPPER PULSE VALVE NUMBER OF PULSES | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TSZ03.HYST | Real | %DB41.DBD2608 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.VALVES.CP8_2CV05 | Bool | %DB45.DBX16.0 | CP8 STEAM DRAIN VALVE 2CV05 SOLENOID | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.BRN_MAIN_CAL_OFFSET | Real | %DB40.DBD384 | BURNER MAIN VACUUM SENSOR CALIBRATION OFFSET VALUE (mBar) | Cyclic in operation | 1 s
RecircAirDamper_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.PID.BICARB_FEED.INTEGRAL | Int | %DB40.DBW1784 | I TERM (TI) | Cyclic in operation | 1 s
STRT ID FANS | Timer | %T110 | MAIN FILTER FANS START DELAY TIMER | Cyclic in operation | 1 s
IDB CP3 DISTRIB SCREW DP.Status | Int | %DB541.DBW2 | Motor Status | Cyclic in operation | 1 s
DB SEND/RECV COOLER 2.SEND.TIMES.MIN_RUN_TIME | Time | %DB162.DBD214 | COOLER MINIMUM RUN TIME | Cyclic in operation | 1 s
S8_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
IDB CP13 PAC FEED SCREW.Status.StatusWord | Int | %DB144.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_PUMP.SP | Real | %DB40.DBD1858 | INTERNAL SETPOINT | Cyclic in operation | 1 s
DB ALARMS TO SCADA.PROCESS.WORD4 | Int | %DB12.DBW110 | PROCESS ALARMS - WORD 4 | Continuous | 1 s
DB ALARM SETPOINTS.CP13R4_1FT02.LOLO | Real | %DB41.DBD1356 | LOW LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_OBSTR_PRESET | Real | %DB40.DBD28 | STOKER 3 OBSTRUCTION ALARM COUNTER PRESET | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2SW12 | Bool | %DB45.DBX12.7 | CP8 ECONOMISER SOOTBLOWER 2 EXTENDED PROXIMITY SWITCH | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD6.CP19_2TT02 | Bool | %DB11.DBX19.7 | CP19 TEMPERATURE AFTER DESUPERHEATER | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_PID_FAN_SPD_OUT_3 | Real | %DB40.DBD164 | STOKER PID AIR FAN SPEED OUTPUT 3 | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_8PT01.HIHI | Real | %DB41.DBD1664 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD7.CP19_2TT05 | Bool | %DB11.DBX20.2 | CP19 SOOTBLOWER STEAM DRAIN TEMPERATURE | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_S2581 | Bool | %DB45.DBX24.1 | CP13 RACK 4 BICARB SILO SURGE HOPPER EMPTY LEVEL PROBE | Cyclic in operation | 1 s
IDB CP2 HYD PUMP.Rem_Cmds.RemoteCtrl | Bool | %DB100.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_PID_FLOW_5 | Real | %DB40.DBD192 | STOKER PID AIR FLOW POINT 5 | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.WOOD_FEED.STK_2_TRAV_INTERVAL | Int | %DB40.DBW884 | STOKER 2 TRAVERSE INTERVAL TIME (SEC) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2SW04 | Bool | %DB45.DBX10.7 | CP8 SUPERHEATER SOOTBLOWER 2 EXTENDED PROXIMITY SWITCH | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_41 | Bool | %DB2.DBX299.0 | Profibus Node | Cyclic in operation | 1 s
FeederScrewPID_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
IDB CP12 ALTERN COOL DP.Load | Real | %DB545.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
DB SETPOINTS.PID.HI_TEMP_CTRL_STEAM.OP_MIN | Real | %DB40.DBD1514 | OUTPUT MIN VALUE (LMN_LLM) | Cyclic in operation | 1 s
DB SAFETY.RECV.CP13d_3PS04 | Bool | %DB44.DBX3.7 | CP13d PLANT AIR PRESSURE HEALTHY (1=HEALTHY) | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK5.ALARM114 | Bool | %DB400.DBX238.2 | CONDENSATE PUMP 2 RUNNING | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.SOOTBLOWERS.CP8_SOOTBLOW_RNG_NB | Int | %DB1.DBW258 | CP8 NUMBER OF SOOTBLOWER RUNNING | Cyclic in operation | 1 s
8CS03_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
SECOND FAN OK AUTOSTART | Bool | %M136.0 | SECONDARY FAN READY / AVAILABLE FOR SYSTEM AUTO START | Cyclic in operation | 1 s
8VAS02_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD5.CP18_1PT02 | Bool | %DB11.DBX17.5 | CP18 MOVING GRATE PRESSURE TRANSMITTER 2 | Cyclic in operation | 1 s
DB SAFETY.RECV.E13c_K436_ON | Bool | %DB44.DBX7.3 | COMBUSTION FAN PANEL CP13d SAFETY CONTACTOR ENERGISED (1=ON) | Cyclic in operation | 1 s
2MTR05_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARMS.COOLERS.COOLER2.WORD2.COMMS_FAULT | Bool | %DB11.DBX136.0 | COMMUNICATION FAULT | Cyclic in operation | 1 s
DB SEND/RECV COOLER 3.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_LO | Real | %DB163.DBD190 | CIRCULATION WATER OUTLET TEMPERATURE LOW ALARM | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_3PI01b.HI | Real | %DB41.DBD1092 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_PID_FAN_SPD_1 | Real | %DB40.DBD240 | STOKER PID AIR FAN SPEED POINT 1 | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP7_U75.HI | Real | %DB41.DBD580 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
IDB CP13 RS SLEW RING DP.Status | Int | %DB557.DBW2 | Motor Status | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_SPARE1.HI | Real | %DB41.DBD1060 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.PUSH_FLOOR.CP2_1SW22_MAX | Bool | %DB45.DBX3.0 | CP2 PUSH FLOOR LADDER No 3 MAXIMUM PROXIMITY | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.STOKER_3_MAN_ST | Bool | %DB1.DBX6.1 | CP3 STOKER 3 TRAVERSE MANUAL START SELECT (SCADA) | Cyclic in operation | 1 s
DB SETPOINTS.PID.BICARB_FEED.OP_MAX | Real | %DB40.DBD1786 | OUTPUT MAX VALUE (LMN_HLM) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD4.CP17_4LC02 | Bool | %DB11.DBX15.1 | CP17 DEAERATOR WATER LEVEL TRANSDUCER (4-20mA = 0-100%) | Cyclic in operation | 1 s
DB LV GEN POWER METER.KVArtot | Real | %DB201.DBD160 | TOTAL REACTIVE POWER (KVAr) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.PUSH_FLOOR.CP2_Q15 | Bool | %DB45.DBX2.1 | CP2 110VAC CONTROL SUPPLY HEALTHY | Cyclic in operation | 1 s
DB SETPOINTS.PID.SECOND_FAN.OP_SCALE | Real | %DB40.DBD1426 | OUTPUT SCALE FACTOR (LMN_FAC) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 5.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_HI | Real | %DB165.DBD186 | CIRCULATION WATER OUTLET TEMPERATURE HIGH ALARM | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_23 | Bool | %DB2.DBX296.6 | Profibus Node | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_PID_FAN_SPD_4 | Real | %DB40.DBD44 | STOKER PID AIR FAN SPEED POINT 4 | Cyclic in operation | 1 s
IDB ST HYD PUMP 1 PBUS.Recv.StatusWord | Word | %DB500.DBW20 | Status Word | Cyclic in operation | 1 s
STRT PAC DOSING | Timer | %T115 | P.A.C. DOSING SYSTEM START DELAY TIMER | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP7_7PLT07.LOLO | Real | %DB41.DBD684 | LOW LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_8LT01.LO | Real | %DB41.DBD1608 | LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD3.CP13R4_1TT10 | Bool | %DB11.DBX13.3 | CP13 RACK 4 PRIMARY AIR TEMPERATURE | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.FILTER.RS_MAINT_VLV_OPN | Bool | %DB1.DBX30.5 | RESIDUE SILO MAINTENANCE BUTTERFLY VALVE MANUAL OPEN SELECT (SCADA) | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.TURBINE_2.REACT_POWER | Real | %DB42.DBD1408 | REACTIVE POWER | Cyclic in operation | 1 s
DB LV GRID POWER METER.M4_PAC3200.PF2 | Real | %DB200.DBD76 | POWER FACTOR PHASE 2 | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP18_1PT01 | Real | %DB42.DBD304 | CP18 MOVING GRATE PRESSURE TRANSMITTER 1 (4-20mA = -500-200 mBar) | Cyclic in operation | 1 s
1MTR13_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.OP_MODES.OP_MODE_9 | Bool | %DB30.DBX9.1 | SYSTEM IN OPERATION MODE 9 (SHUTDOWN 3 - COOLING) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_SPD_OFFSET | Real | %DB40.DBD224 | STOKER SPEED OFFSET | Cyclic in operation | 1 s
CP7 AUTO C_OVER OCC | Bool | %M142.3 | CP7 BOILER FEED PUMP AUTO CHANGEOVER OCCURED | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BOILER.STEAM_STOP_VLV_OPN | Bool | %DB1.DBX22.4 | CP8 STEAM STOP VALVE MANUAL OPEN SELECT (SCADA) | Cyclic in operation | 1 s
EXEC MODE No REQ | Int | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.START.TIMERS.PAC_DOSING | S5Time | %DB30.DBW160 | P.A.C. DOSING SYSTEM | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.LO.WORD4.CP17_8LT01 | Bool | %DB11.DBX56.2 | CP17 PLANT WATER TANK LEVEL TRANSDUCER (4-20mA = 0-100%) | Cyclic in operation | 1 s
IDB CP13 RS HORIZ SCREW.Rem_Cmds.RunFwd | Bool | %DB134.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB SETPOINTS.PID.PRIM_FAN.MANUAL_VAL | Real | %DB40.DBD1362 | PID OUTPUT IN MANUAL (MAN) | Cyclic in operation | 1 s
3Pw482_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARMS TO SCADA.SUPPLIES.WORD4 | Int | %DB12.DBW92 | POWER SUPPLY ALARMS - WORD 4 | Continuous | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP19_2PT05 | Real | %DB42.DBD364 | CP19 SOOTBLOWER STEAM PRESSURE (4-20mA = 0-63 Bar) | Cyclic in operation | 1 s
IDB CP5 OIL BURNER.Status.StatusWord | Int | %DB125.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.BURNER.BRN_BKUP_VAC_CAL_VAL | Real | %DB42.DBD1232 | BURNER VACUUM SENSOR 1PT02 CALIBRATED VALUE (mBar) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BURNER.O2_PURGE_ON | Bool | %DB1.DBX39.0 | O2 METER PURGE MANUAL ON SELECT (SCADA) | Cyclic in operation | 1 s
DB MV TURB POWER METER.KVA3 | Real | %DB202.DBD124 | APPARANT POWER PHASE 3 (KVA) | Cyclic in operation | 1 s
DB SETPOINTS.PID.BICARB_FEED.OP_OFFSET | Real | %DB40.DBD1798 | OUTPUT OFFSET (LMN_OFF) | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_35 | Bool | %DB2.DBX298.2 | Profibus Node | Cyclic in operation | 1 s
DB ALARMS TO SCADA.SULPHUR_DOS.WORD2 | Int | %DB12.DBW128 | SULPHUR DOSING ALARMS - WORD 2 | Continuous | 1 s
DB SYSTEM CONTROL.GENERAL.MAIN_CTRL.EXEC_OVERRIDE_EN | Bool | %DB30.DBX0.7 | SYSTEM EXECUTIVE OVERRIDE MODE ENABLE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_3TI01b.HYST | Real | %DB41.DBD1040 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.LO.WORD6.CP19_2LT01 | Bool | %DB11.DBX60.3 | CP19 DP CELL WATER LEVEL | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.PUSH_FLOOR.CP2_LAD_2_INSERV | Bool | %DB1.DBX2.5 | CP2 PUSH FLOOR LADDER 2 IN SERVICE | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.BOILER_FEED_WATER_VLV.OUTPUT | Real | %DB42.DBD1608 | OUTPUT VALUE | Cyclic in operation | 1 s
DB SEND/RECV COOLER 4.SEND.GENERAL.START_COOLER | Bool | %DB164.DBX70.5 | <No Value> | Cyclic in operation | 1 s
IDB CP12 ALTERNTR COOLER.Rem_Cmds.RunFwd | Bool | %DB173.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD4.CP17_8LT04 | Bool | %DB11.DBX14.3 | CP17 TREATED WATER TANK LEVEL TRANSDUCER (4-20mA = 0-100%) | Cyclic in operation | 1 s
STRT 1MTR03 | Timer | %T53 | CP2 SCRAPER CHAIN CONVEYOR START DELAY TIMER | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_PUMP.CYCLE_TIME | Int | %DB40.DBW1866 | SAMPLE TIME (CYCLE) | Cyclic in operation | 1 s
DB SETPOINTS.PID.ID_FAN.INTEGRAL | Int | %DB40.DBW1278 | I TERM (TI) | Cyclic in operation | 1 s
DB SETPOINTS.PID.RECIRC_FAN.SP | Real | %DB40.DBD1306 | INTERNAL SETPOINT | Cyclic in operation | 1 s
1HR02_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB LV GEN POWER METER.KVAtot | Real | %DB201.DBD152 | TOTAL APPARANT POWER (KVA) | Cyclic in operation | 1 s
IDB FEED PUMP 2 PBUS.Status.Load | Real | %DB509.DBD42 | Drive Load in Percentage (%) | Cyclic in operation | 1 s
IDB REC AIR FAN PBUS.Recv.StatusWord | Word | %DB515.DBW24 | Status Word | Cyclic in operation | 1 s
DB SETPOINTS.PID.STOKER_1.SP | Real | %DB40.DBD1444 | INTERNAL SETPOINT | Cyclic in operation | 1 s
DB ALARMS.COOLERS.COOLER4.WORD2.COMMS_FAULT | Bool | %DB11.DBX144.0 | COMMUNICATION FAULT | Cyclic in operation | 1 s
CP3 1SW16 FLT | Bool | %M64.2 | CP3 SCRAPER CHAIN CONVEYOR TENSION MONITOR 1 FAULT | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.FILTER.RS_VIB_STAT | Int | %DB1.DBW234 | RESIDUE SILO VIBRATOR STATUS | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_S254 | Bool | %DB45.DBX22.0 | CP13 RACK 4 RESIDUE SILO MAINTENANCE BUTTERFLY VALVE CLOSED | Cyclic in operation | 1 s
CP8 START SOOTBLOW | Bool | %M88.1 | CP8 START SOOTBLOWERS | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MAIN_CTRL.FEED_PUMPS_START | Bool | %DB30.DBX1.1 | START BOILER FEED PUMP(S) (FROM SCADA) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TSZ03.HIHI | Real | %DB41.DBD2592 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.FEED_WTR_TANK_PRDS_CTRL.CURR_SP | Real | %DB42.DBD1562 | CURRENT RAMP SETPOINT | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.BURNER.CP18_1SW47 | Bool | %DB45.DBX15.3 | CP18 GRATE 2 REVERSE SWITCH 2 | Cyclic in operation | 1 s
S6_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_K2721 | Bool | %DB45.DBX21.3 | CP13 RACK 4 FILTER 2 INLET VALVE A OPEN SOLENOID 3VAS01a1 | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.WOOD_FEED.STK_3_PID_SEL_PV | Int | %DB1.DBW188 | CP3 STOKER 3 FEED PID (0 = STANDARD, 1 = LAMBDA, 2 = FAN SPEED, 3 = AIR FLOW) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BOILER.STEAM_DRAIN_VLV_OPN | Bool | %DB1.DBX22.2 | CP8 STEAM DRAIN VALVE MANUAL OPEN SELECT (SCADA) | Cyclic in operation | 1 s
IDB CP13 FILTER SEAL B.Rem_Cmds.RemoteCtrl | Bool | %DB129.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB PROCESS VALUES.EMISSIONS.CO2_PCT | Real | %DB42.DBD808 | CARBON DIOXIDE CO2 (%) | Continuous | 1 s
DB PROCESS VALUES.ANALOGUE.OUTPUTS.CP17_2CV07_REF | Real | %DB42.DBD624 | CP17 PRESSURE REDUCING DESUPERHEATER VALVE HP STEAM TO FW TANK (4-20mA = 0-100% | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_SPD_OFFSET | Real | %DB40.DBD328 | STOKER SPEED OFFSET | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_PID_FLOW_OUT_1 | Real | %DB40.DBD300 | STOKER PID AIR FLOW OUTPUT 1 | Cyclic in operation | 1 s
DB ALARMS TO SCADA.SULPHUR_DOS.WORD1 | Int | %DB12.DBW126 | SULPHUR DOSING ALARMS - WORD 1 | Continuous | 1 s
IDB CP3 GRATE HYD PMP 2.Status.Running | Bool | %DB116.DBX20.7 | Motor Running | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP18_1TT06 | Real | %DB42.DBD276 | CP18 STOKER TEMPERATURE PROBE 2 (PT100) (0-150 ºC) | Cyclic in operation | 1 s
DB MV TURB POWER METER.M6_PAC3200.I2 | Real | %DB202.DBD28 | CURRENT PHASE 2 (AMPS) | Cyclic in operation | 1 s
IDB ST HYD PUMP 3 PBUS.Status.ErrorCode | Int | %DB502.DBW46 | Last Trip Code | Cyclic in operation | 1 s
DB MV TURB POWER METER.KVAr3 | Real | %DB202.DBD148 | REACTIVE POWER PHASE 3 (KVAr) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP7_7PLT07.HI | Real | %DB41.DBD676 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_TEMP_CTRL.OP_SCALE | Real | %DB40.DBD1748 | OUTPUT SCALE FACTOR (LMN_FAC) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_PID_FLOW_OUT_1 | Real | %DB40.DBD196 | STOKER PID AIR FLOW OUTPUT 1 | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD3.CP19_2CV02_TIMEOUT | Bool | %DB11.DBX109.3 | CP19 SUPERHEATER 2 BLOW OUT VALVE TIMEOUT ALARM | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4PT01.HIHI | Real | %DB41.DBD1728 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.TURBINE_2.VOLT_L3_L1 | Real | %DB42.DBD1420 | VOLTAGE L3-L1 | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_2FT01.HIHI | Real | %DB41.DBD2016 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
1MTR15_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.LO.WORD6 | Int | %DB12.DBW60 | LOW ALARMS - WORD 6 | Continuous | 1 s
DB SYSTEM CONTROL.FILTER.START.BITS.PAC_DOSING | Bool | %DB30.DBX148.5 | P.A.C. DOSING SYSTEM | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.WOOD_FEED.FUEL_DAMPER_TIMEOUT | Int | %DB40.DBW896 | FUEL DAMPER TIMEOUT ALARM TIME (SEC) | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.TURBINE_2.EXH_PRESS | Real | %DB42.DBD1400 | EXHAUST STEAM PRESSURE | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.CP8_SOOTB_7_INSERV | Bool | %DB1.DBX21.6 | CP8 SOOTBLOWER 7 IN SERVICE | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD6.CP3_CHEM_TANK_2_LVL_LO | Bool | %DB11.DBX114.6 | CP3 LOW PRESSURE PUMP 2 CHEMICAL TANK LEVEL LOW ALARM | Cyclic in operation | 1 s
IDB CP13 RS SLEW RING DP.Load | Real | %DB557.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2LT01.HIHI | Real | %DB41.DBD2656 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
IDB CP13 UREA SKID SYS.Rem_Cmds.RemoteCtrl | Bool | %DB148.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB LV GRID POWER METER.KVAr1 | Real | %DB200.DBD140 | REACTIVE POWER PHASE 1 (KVAr) | Cyclic in operation | 1 s
DB SETPOINTS.PID.BICARB_FEED.MANUAL_VAL | Real | %DB40.DBD1776 | PID OUTPUT IN MANUAL (MAN) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_S2561 | Bool | %DB45.DBX23.5 | CP13 RACK 4 BICARB SILO PRESSURE SWITCH | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.HI.WORD4.CP17_4PT01 | Bool | %DB11.DBX42.6 | CP17 DEAERATOR PRESSURE TRANSDUCER (4-20mA = xx Bar) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.STOP.BITS.DISTRIB_SCREW_1MTR10 | Bool | %DB30.DBX110.6 | HOPPER DISTRIBUTION SCREW | Cyclic in operation | 1 s
IDB CP3 ASH SCRAPER CONV.Rem_Cmds.RunFwd | Bool | %DB111.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB SETPOINTS.PID.OIL_BURNER.OP_MIN | Real | %DB40.DBD1698 | OUTPUT MIN VALUE (LMN_LLM) | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.WOOD_FEED.STK_PID_AIR_LAMBDA | Real | %DB42.DBD992 | CP3 STOKER PID AIR LAMBDA | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2MTR02_REV | Bool | %DB45.DBX10.5 | CP8 SUPERHEATER SOOTBLOWER 2 MOTOR RUN REVERSE | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BURNER.RECIRC_DAMPER_MD | Bool | %DB1.DBX38.2 | CP13 RECIRCULATION AIR DAMPER MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2SW08 | Bool | %DB45.DBX11.7 | CP8 BOILER SOOTBLOWER 2 EXTENDED PROXIMITY SWITCH | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BOILER.ONE_FEED_PUMP_RNG | Bool | %DB1.DBX22.0 | CP7 AT LEAST ONE BOILER FEED PUMP IS RUNNING (SCADA) | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP13R4_U112_DP | Real | %DB42.DBD104 | CP13 RACK 4 FILTER 1 DIFFERENTIAL PRESSURE (4..20mA = -10 to +100mBar) | Cyclic in operation | 1 s
IDB CP13 BS AGITATOR DP.Load | Real | %DB552.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.EQUIP_STATUS.RC_TEMP_BEL_SHUT_TEMP | Bool | %DB30.DBX13.1 | RESIDENCE CHAMBER TEMPERATURE IS BELOW SHUTDOWN TEMPERATURE | Cyclic in operation | 1 s
DB SETPOINTS.PID.SECOND_FAN.CYCLE_TIME | Int | %DB40.DBW1406 | SAMPLE TIME (CYCLE) | Cyclic in operation | 1 s
DB MV TURB POWER METER.M6_PAC3200.PFtot | Real | %DB202.DBD100 | TOTAL POWER FACTOR | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FEED_LINE.CP18_1LS02 | Bool | %DB45.DBX6.4 | CP18 STOKER LEVEL SENSOR 1 | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK1.GEARBOX_VIB | DInt | %DB400.DBD60 | VIBRATION MONITORING AT GEARBOX mm/s (x100) | Cyclic in operation | 1 s
IDB CP3 DISTRIB SCREW.Rem_Cmds.Direction | Bool | %DB110.DBX18.4 | 0 = Forward / 1 = Reverse | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_3LO01.HYST | Real | %DB41.DBD912 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB SETPOINTS.PID.SECOND_FAN.OP_MAX | Real | %DB40.DBD1418 | OUTPUT MAX VALUE (LMN_HLM) | Cyclic in operation | 1 s
DB SAFETY.RECV.SYSTEM_ESR_OK | Bool | %DB44.DBX0.3 | Main System Emergency Stop Healthy (1=healthy) | Cyclic in operation | 1 s
8MTR03_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SEND/RECV COOLER 2.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_HIHI | Real | %DB162.DBD182 | CIRCULATION WATER OUTLET TEMPERATURE HIGH HIGH ALARM | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.BURNER.GRT_1_STATUS | Int | %DB1.DBW146 | CP3 GRATE 1 SOLENOIDS STATUS (SCADA DISPLAY) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MAIN_CTRL.OP_MODE_1_SEL | Bool | %DB30.DBX0.5 | OP MODE 1 (AUTO OFF) REQUEST (FROM SCADA) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_S238 | Bool | %DB45.DBX22.5 | CP13 RACK 4 FILTER 2 HOPPER LEVEL PROBE | Cyclic in operation | 1 s
DB LV GRID POWER METER.M4_PAC3200.V2_N | Real | %DB200.DBD4 | VOLTS PHASE 2 TO NEUTRAL (VOLTS) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MAIN_CTRL.WOOD_FEED_START | Bool | %DB30.DBX1.5 | START WOOD FEED (FROM SCADA) | Cyclic in operation | 1 s
DB SETPOINTS.PID.BOILER_FEED_WATER_VLV.OP_OFFSET | Real | %DB40.DBD1246 | OUTPUT OFFSET (LMN_OFF) | Cyclic in operation | 1 s
CP7 8PU03 SELECTED | Bool | %M152.1 | CP7 MAIN PLANT WATER PUMP DUTY SELECTED | Cyclic in operation | 1 s
IDB CP13 PAC AGITATOR.Rem_Cmds.RunFwd | Bool | %DB143.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD4.CP17_4TT01 | Bool | %DB11.DBX15.3 | CP17 DEAERATOR WATER TEMPERATURE PROBE (4-20mA = xx ºC) | Cyclic in operation | 1 s
DB ALARMS TO SCADA.PROCESS.WORD3 | Int | %DB12.DBW108 | PROCESS ALARMS - WORD 3 | Continuous | 1 s
DB SAFETY.RECV.OS13b_ESPB_OK | Bool | %DB44.DBX2.7 | FILTER OPERATOR PENDANT OS13b EM STOP P/BUTTON HEALTHY (1=HEALTHY) | Cyclic in operation | 1 s
DB SETPOINTS.PID.HI_PRESS_CTRL_STEAM.OP_MAX | Real | %DB40.DBD1556 | OUTPUT MAX VALUE (LMN_HLM) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BURNER.PRIM_DAMPER_MD | Bool | %DB1.DBX38.0 | CP13 PRIMARY AIR DAMPER MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_PID_FLOW_2 | Real | %DB40.DBD180 | STOKER PID AIR FLOW POINT 2 | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BOILER.DEAERATOR_OVERFL_VLV_MD | Bool | %DB1.DBX23.2 | CP17 DEAERATOR OVERFLOW VALVE MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.SOOTBLOWERS.SHEAT_1_NB_2 | Int | %DB40.DBW1026 | SUPERHEATER SOOTBLOWER 1 NUMBER 2 | Cyclic in operation | 1 s
STOP FILTER PLANT | Timer | %T104 | BAG FILTER PLANT AND PULSE CONTROLLERS STOP DELAY TIMER | Cyclic in operation | 1 s
DB LV GEN POWER METER.KVAr1 | Real | %DB201.DBD140 | REACTIVE POWER PHASE 1 (KVAr) | Cyclic in operation | 1 s
CP7 8PU03/04 SELECT | Bool | %M152.0 | CP7 PLANT WATER PUMP DUTY REQUEST (SCADA) (0=MAIN. 1=STANDBY) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.STOP.TIMERS.PAC_DOSING | S5Time | %DB30.DBW184 | P.A.C. DOSING SYSTEM | Cyclic in operation | 1 s
TRIPS OK | Bool | %M30.2 | SYSTEM TRIPS HEALTHY | Cyclic in operation | 1 s
IDB CP2 HYD PUMP HTR DP.Status | Int | %DB520.DBW2 | Motor Status | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.SECOND_AIR_FAN.O2_PID_O2_SP_2 | Real | %DB40.DBD756 | SECONDARY AIR FAN PID CONTROLLER O2 SETPOINT 2 | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_1_SPD_MANUAL | Real | %DB40.DBD484 | GRATE MANUAL SPEED | Cyclic in operation | 1 s
DB SEND/RECV COOLER 6.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_HI | Real | %DB166.DBD186 | CIRCULATION WATER OUTLET TEMPERATURE HIGH ALARM | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.SECOND_AIR_FAN.O2_PID_O2_SP_4 | Real | %DB40.DBD764 | SECONDARY AIR FAN PID CONTROLLER O2 SETPOINT 4 | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD4.CP17_4CV03_POS | Bool | %DB11.DBX15.0 | CP17 FEEDWATER TO DESUPERHEATER CONTROL VALVE ACTUAL POSITION (4-20mA = 0-100%) | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP18_1TT03 | Real | %DB42.DBD296 | CP18 RESIDENCE CHAMBER TEMPERATURE PROBE 2 | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_44 | Bool | %DB2.DBX299.3 | Profibus Node | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_PID_FAN_SPD_5 | Real | %DB40.DBD152 | STOKER PID AIR FAN SPEED POINT 5 | Cyclic in operation | 1 s
IDB CP21 SULPHUR DOS SYS.Status.StatusWord | Int | %DB124.DBW22 | Motor Status Word | Cyclic in operation | 1 s
MODE 3 Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SAFETY.RECV.CP19_2PSZ02 | Bool | %DB44.DBX4.6 | BOILER PANEL CP19 HI STEAM DRUM PRESSURE TRIP (1=HEALTHY) | Cyclic in operation | 1 s
DB SETPOINTS.PID.BICARB_FEED_HCL.INTEGRAL | Int | %DB40.DBW2106 | I TERM (TI) | Cyclic in operation | 1 s
DB SAFETY.RECV.OS2_2_ESPB_OK | Bool | %DB44.DBX2.2 | PUSH FLOOR STATION OS2.2 EM STOP P/BUTTON HEALTHY (1=HEALTHY) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.CP8_SOOTB_2_INSERV | Bool | %DB1.DBX21.1 | CP8 SOOTBLOWER 2 IN SERVICE | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.STOP.BITS.LEV_SCREW_1MTR02 | Bool | %DB30.DBX110.1 | LEVELLING SCREW | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.VALVES.CP8_2SW16 | Bool | %DB45.DBX16.5 | CP8 STEAM STOP VALVE 2CV06 CLOSED FEEDBACK | Cyclic in operation | 1 s
DB ALARMS TO SCADA.REMOTE.WORD1 | Int | %DB12.DBW82 | REMOTE ALARMS - WORD 1 | Continuous | 1 s
DB LV GRID POWER METER.KVAr3 | Real | %DB200.DBD148 | REACTIVE POWER PHASE 3 (KVAr) | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_40 | Bool | %DB2.DBX298.7 | Profibus Node | Cyclic in operation | 1 s
IDB CP3 DISTRIB SCREW.Rem_Cmds.Run | Bool | %DB110.DBX18.3 | 0 = Stop / 1 = Run in Selected Direction | Cyclic in operation | 1 s
DB SEND/RECV COOLER 5.SEND.GENERAL.START_COOLER | Bool | %DB165.DBX70.5 | <No Value> | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.HIHI.WORD6 | Int | %DB12.DBW32 | HIGH HIGH ALARMS - WORD 6 | Continuous | 1 s
IDB FEED PUMP 1 PBUS.Status.ErrorCode | Int | %DB508.DBW46 | Last Trip Code | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_26 | Bool | %DB2.DBX297.1 | Profibus Node | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.EQUIP_STATUS.ID_FAN_IS_ON | Bool | %DB30.DBX14.0 | ID FAN IS RUNNING (TIMED ON) | Cyclic in operation | 1 s
DB SETPOINTS.PID.OIL_BURNER.OP_MAX | Real | %DB40.DBD1694 | OUTPUT MAX VALUE (LMN_HLM) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4TT01.LOLO | Real | %DB41.DBD1900 | LOW LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MAIN_CTRL.AUTO_START | Bool | %DB30.DBX0.2 | SYSTEM AUTO START REQUEST (FROM SCADA) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 6.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_HIHI | Real | %DB166.DBD182 | CIRCULATION WATER OUTLET TEMPERATURE HIGH HIGH ALARM | Cyclic in operation | 1 s
DB SETPOINTS.PID.SECOND_FAN.RAMP_EN | Bool | %DB40.DBX1434.2 | RAMP ENABLED (1=ENABLED) | Cyclic in operation | 1 s
IDB ST HYD PUMP 2 PBUS.Send.ControlWord | Word | %DB501.DBW8 | Control Word | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MODE_STATUS.EXEC_OPMODE_1_STAT | Int | %DB30.DBW34 | EXECUTIVE OVERRIDE MODE 1 STATUS (0=NOT SEL, 1=REQ, 2=REQ & ACHIEVED) | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.TURBINE.COND_LVL | Real | %DB42.DBD1132 | TURBINE CONDENSATE WATER LEVEL | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.SOOTBLOWERS.BOILER_2_NB_1 | Int | %DB40.DBW1018 | BOILER SOOTBLOWER 2 NUMBER 1 | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_2TT06.HIHI | Real | %DB41.DBD2048 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.WOOD_FEED.STK_3_TRAV_MAX_TIMEOUT | Int | %DB40.DBW890 | STOKER 3 TRAVERSE MAXIMUM TIMEOUT TIME (SEC) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_2_SPD_OFFSET | Real | %DB40.DBD528 | GRATE SPEED OFFSET | Cyclic in operation | 1 s
DB SETPOINTS.PID.BOILER_FEED_WATER_VLV.RAMP_RATE | Real | %DB40.DBD1218 | RAMP TO SETPOINT RATE | Cyclic in operation | 1 s
DB SEND/RECV COOLER 2.RECV.PROCESS_VALUES.COOL_FAN_ACT_SPD | Real | %DB162.DBD26 | COOLING FANS ACTUAL SPEED | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.PUSH_FLOOR.CP2_LAD_6_INSERV | Bool | %DB1.DBX3.1 | CP2 PUSH FLOOR LADDER 6 IN SERVICE | Cyclic in operation | 1 s
IDB CP13 BS FEED SCREW.Rem_Cmds.RemoteCtrl | Bool | %DB140.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SAFETY.RECV.E13c_K454_ON | Bool | %DB44.DBX5.6 | SECONDARY AIR FAN MOTOR 3MTR11 ISOLATION CONTACTOR (0=ISOLATED) | Cyclic in operation | 1 s
IDB GR HYD PUMP 2 PBUS.Recv.StatusWord | Word | %DB504.DBW20 | Status Word | Cyclic in operation | 1 s
IDB ST HYD PUMP 1 PBUS.Status.Load | Real | %DB500.DBD42 | Drive Load in Percentage (%) | Cyclic in operation | 1 s
IDB CP3 GRATE HYD PMP 1.Status.StatusWord | Int | %DB115.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP13R4_1TT11 | Real | %DB42.DBD180 | CP13 RACK 4 SECONDARY AIR TEMPERATURE (4..20mA = 0 to 400ºC) | Cyclic in operation | 1 s
DB SETPOINTS.PID.ID_FAN.RAMP_RATE | Real | %DB40.DBD1264 | RAMP TO SETPOINT RATE | Cyclic in operation | 1 s
IDB GR HYD PUMP 2 PBUS.Status.ErrorCode | Int | %DB504.DBW46 | Last Trip Code | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK2.V_WIND_TEMP | DInt | %DB400.DBD72 | WINDING TEMPERATURE V DEG C (x100) | Cyclic in operation | 1 s
SootB_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SEND/RECV COOLER 1.RECV.GENERAL.FANS_STATUS | Int | %DB161.DBW4 | COOLER FANS STATUS | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_PID_FAN_SPD_2 | Real | %DB40.DBD140 | STOKER PID AIR FAN SPEED POINT 2 | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.RECIRC_FAN.PID_ACTV | Bool | %DB42.DBX1650.1 | PID CONTROLLER ACTIVE | Cyclic in operation | 1 s
Trend_Scale_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.WOOD_FEED.STK_1_TRAV_MAX_TIMEOUT | Int | %DB40.DBW882 | STOKER 1 TRAVERSE MAXIMUM TIMEOUT TIME (SEC) | Cyclic in operation | 1 s
DB LV GRID POWER METER.M4_PAC3200.I3 | Real | %DB200.DBD32 | CURRENT PHASE 3 (AMPS) | Cyclic in operation | 1 s
1PT012_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP19_3EM01 | Real | %DB42.DBD368 | CP19 FLUE GAS OXYGEN LEVEL (4..20mA - 0.5-20.9%) (O2) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 2.RECV.GENERAL.WATCHDOG | Bool | %DB162.DBX0.0 | <No Value> | Cyclic in operation | 1 s
DB LV GEN POWER METER.M5_PAC3200.V2_V3 | Real | %DB201.DBD16 | VOLTS PHASE 2 TO PHASE 3 (VOLTS) | Cyclic in operation | 1 s
IDB CP3 STOKER HYD PMP 1.Rem_Cmds.RunFwd | Bool | %DB112.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.CP8_SOOTB_3_INSERV | Bool | %DB1.DBX21.2 | CP8 SOOTBLOWER 3 IN SERVICE | Cyclic in operation | 1 s
3MTR07_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT09.HI | Real | %DB41.DBD2500 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SEND/RECV COOLER 2.RECV.GENERAL.PUMP_STATUS | Int | %DB162.DBW2 | COOLER PUMP STATUS | Cyclic in operation | 1 s
DB LV GRID POWER METER.KVA3 | Real | %DB200.DBD124 | APPARANT POWER PHASE 3 (KVA) | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_TEMP_CTRL.INTEGRAL | Int | %DB40.DBW1738 | I TERM (TI) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BICARB_FEED.SO2_START_FEED | Real | %DB40.DBD804 | SO2 SETPOINT TO START BICARB FEEDING | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BURNER.BRN_TEMP_1TT03_IN_USE | Bool | %DB1.DBX36.6 | RESIDANCE CHAMBER TEMPERATURE PROBE 1TT03 VALUE IN USE | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.OPN_SHT.WORD4 | Int | %DB12.DBW14 | OPEN/SHORT CIRCUIT ALARMS - WORD 4 | Continuous | 1 s
IDB CP13 BS AGITATOR.Rem_Cmds.RunFwd | Bool | %DB139.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_LOW_SPD | Real | %DB40.DBD348 | MIDDLE STOKER LOW SPEED WHEN 1PS03 ACTIVE | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.OPN_SHT.WORD2 | Int | %DB12.DBW10 | OPEN/SHORT CIRCUIT ALARMS - WORD 2 | Continuous | 1 s
IDB CP3 DISTRIB SCREW.Status.Running | Bool | %DB110.DBX20.7 | Motor Running | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_6 | Bool | %DB2.DBX294.5 | Profibus Node | Cyclic in operation | 1 s
DB ALARMS.ESTOPS.WORD2.CP19_2PSZ02 | Bool | %DB11.DBX80.6 | BOILER PANEL CP19 HI STEAM DRUM PRESSURE TRIP | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD4.CP17_8PT01 | Bool | %DB11.DBX14.4 | CP17 PLANT WATER PRESSURE TRANSDUCER (4-20mA = xx Bar) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_PID_FAN_SPD_3 | Real | %DB40.DBD144 | STOKER PID AIR FAN SPEED POINT 3 | Cyclic in operation | 1 s
IDB CP7 HP DOSING PUMP.Rem_Cmds.RemoteCtrl | Bool | %DB184.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD2.CP7_7TT06 | Bool | %DB11.DBX10.4 | CP7 COOLING CIRCULATION WATER RETURN TEMPERATURE | Cyclic in operation | 1 s
CP2 PS 1SW02 FLT | Bool | %M58.6 | CP2 SCRAPER CHAIN CONVEYOR TENSIONER No 2 FAULT | Cyclic in operation | 1 s
DB SETPOINTS.PID.COOLERS.SP | Real | %DB40.DBD2042 | INTERNAL SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_SPD_FACTOR | Real | %DB40.DBD124 | STOKER SPEED FACTOR | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_8LT01.HIHI | Real | %DB41.DBD1600 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.PID.RECIRC_FAN.OP_MIN | Real | %DB40.DBD1330 | OUTPUT MIN VALUE (LMN_LLM) | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_36 | Bool | %DB2.DBX298.3 | Profibus Node | Cyclic in operation | 1 s
DB SEND/RECV COOLER 6.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_HYST | Real | %DB166.DBD198 | CIRCULATION WATER OUTLET TEMPERATURE ALARM HYSTERESIS | Cyclic in operation | 1 s
DB SEND/RECV COOLER 6.SEND.GENERAL.REMOTE_RUN | Bool | %DB166.DBX70.7 | 0 = STOP / 1 = RUN | Cyclic in operation | 1 s
STRT 1MTR02 | Timer | %T55 | CP2 LEVELLING SCREW START DELAY TIMER | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_3TI01c.HIHI | Real | %DB41.DBD1120 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARMS TO SCADA.COOLERS.COOLER3.WORD1 | Int | %DB12.DBW138 | COOLER 3 ALARMS - WORD 1 | Continuous | 1 s
DB SETPOINTS.TIMERS.SOOTBLOWERS.BOILER_1_NB_1 | Int | %DB40.DBW1016 | BOILER SOOTBLOWER 1 NUMBER 1 | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TT07.HYST | Real | %DB41.DBD3280 | ALARM HISTERESYS | Cyclic in operation | 1 s
PRIM FAN OK AUTOSTART | Bool | %M134.0 | PRIMARY FAN READY / AVAILABLE FOR SYSTEM AUTO START | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1PT01.HYST | Real | %DB41.DBD2448 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB LV GEN POWER METER.KVAr3 | Real | %DB201.DBD148 | REACTIVE POWER PHASE 3 (KVAr) | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP17_2PT06 | Real | %DB42.DBD212 | CP17 FEEDWATER TANK STEAM BLEED PRESSURE TRANSDUCER (4-20mA = 0-55 Bar) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MODE_STATUS.EXEC_OPMODE_5_STAT | Int | %DB30.DBW42 | EXECUTIVE OVERRIDE MODE 5 STATUS (0=NOT SEL, 1=REQ, 2=REQ & ACHIEVED) | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD1.CP2_LEV_AUG_ROT | Bool | %DB11.DBX104.5 | CP2 LEVELLING AUGER ROTATION FAULT | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_3TI01a.HI | Real | %DB41.DBD996 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.STOP.BITS.ID_FANS | Bool | %DB30.DBX182.3 | MAIN FILTER FANS | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BURNER.RECIRC_FAN_SENS_IN_USE | Bool | %DB1.DBX38.5 | CP13 RECIRCULATION AIR FAN TEMPERATURE SENSOR IN USE (0 = 1TT01, 1 = 1TT02,3,4) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.EQUIP_STATUS.BC_GRATES_ARE_OFF | Bool | %DB30.DBX12.2 | COMBUSTION CHAMBER GRATES ARE OFF | Cyclic in operation | 1 s
DB SEND/RECV COOLER 6.SEND.GENERAL.START_ADIABATIC | Bool | %DB166.DBX71.0 | <No Value> | Cyclic in operation | 1 s
1GR01_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SEND/RECV COOLER 1.RECV.PROCESS_VALUES.COOL_FAN_ACT_SPD | Real | %DB161.DBD26 | COOLING FANS ACTUAL SPEED | Cyclic in operation | 1 s
DB LV GRID POWER METER.M4_PAC3200.HZ | Real | %DB200.DBD84 | FREQUENCY (HZ) | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.FILTER.FILT2_PULSE_CTRL_STAT | Int | %DB1.DBW224 | FILTER 2 PULSE CONTROLLER STATUS | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4PLT03.HYST | Real | %DB41.DBD2000 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP7_7PLT07.HYST | Real | %DB41.DBD688 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP7_7TT07.HIHI | Real | %DB41.DBD608 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.HIHI.WORD5 | Int | %DB12.DBW30 | HIGH HIGH ALARMS - WORD 5 | Continuous | 1 s
IDB ST HYD PUMP 3 PBUS.Recv.StatusWord | Word | %DB502.DBW20 | Status Word | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT06.HIHI | Real | %DB41.DBD2208 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
ID FAN SOOTH MD | Bool | %M106.2 | ID FANS IN SOOTHING MODE | Cyclic in operation | 1 s
DB ALARMS TO SCADA.COOLERS.COOLER1.WORD1 | Int | %DB12.DBW130 | COOLER 1 ALARMS - WORD 1 | Continuous | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP19_2TT05 | Real | %DB42.DBD392 | CP19 SOOTBLOWER STEAM DRAIN TEMPERATURE (TC) (0-450 ºC) | Cyclic in operation | 1 s
11RMC6F_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
IDB CP12 TURBINE COOL DP.Status | Int | %DB537.DBW2 | Motor Status | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_TEMP_CTRL.MAN_AUTO | Bool | %DB40.DBX1756.0 | PID MANUAL/AUTO MODE (1=MANUAL) (MAN_ON) | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP17_8PT01 | Real | %DB42.DBD208 | CP17 PLANT WATER PRESSURE TRANSDUCER (4-20mA = 0-10 Bar) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 3.SEND.GENERAL.REMOTE_AUTO | Bool | %DB163.DBX70.6 | 0 = REMOTE MANUAL / 1 = REMOTE AUTO | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_12 | Bool | %DB2.DBX295.3 | Profibus Node | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.BURNER.CP18_K95 | Bool | %DB45.DBX14.0 | CP18 MOVING GRATE 1 FORWARD SOLENOID 1CV16 (UPPER LEFT) | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.FEED_WTR_TANK_TEMP_CTRL.OUTPUT | Real | %DB42.DBD1938 | OUTPUT VALUE | Cyclic in operation | 1 s
STOP ID FANS | Timer | %T103 | MAIN FILTER FANS STOP DELAY TIMER | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.EQUIP_STATUS.STOKERS_ON | Bool | %DB30.DBX12.4 | STOKERS ARE RUNNING (PURGING) | Cyclic in operation | 1 s
DB SETPOINTS.PID.BOILER_FEED_WATER_VLV.GAIN | Real | %DB40.DBD1228 | P TERM (GAIN) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.STK_1_PID_MTHD_3_SEL | Bool | %DB1.DBX7.3 | STOKER 1 PID CONTROLLER METHOD 3 SELECTED | Cyclic in operation | 1 s
IDB FEED PUMP 1 PBUS.Status.Load | Real | %DB508.DBD42 | Drive Load in Percentage (%) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 2.SEND.GENERAL.START_ADIABATIC | Bool | %DB162.DBX71.0 | <No Value> | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2MTR07_FWD | Bool | %DB45.DBX13.0 | CP8 ECONOMISER SOOTBLOWER 3 MOTOR RUN FORWARD | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.EQUIP_STATUS.SECON_FAN_IS_OFF | Bool | %DB30.DBX12.7 | SECONDARY AIR FAN IS OFF | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.ID_FAN.CURR_SP | Real | %DB42.DBD1622 | CURRENT RAMP SETPOINT | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2MTR03_FWD | Bool | %DB45.DBX11.0 | CP8 BOILER SOOTBLOWER 1 MOTOR RUN FORWARD | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.FILTER.RES_SILO_ARM_MD | Bool | %DB1.DBX29.2 | RESIDUE SILO ARM MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.START.BITS.FILTER_PLANT | Bool | %DB30.DBX148.2 | BAG FILTER PLANT AND PULSE CONTROLLERS | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2MTR03_REV | Bool | %DB45.DBX11.1 | CP8 BOILER SOOTBLOWER 1 MOTOR RUN REVERSE | Cyclic in operation | 1 s
DB SETPOINTS.PID.SECOND_FAN.INTEGRAL | Int | %DB40.DBW1416 | I TERM (TI) | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.FEED_WTR_TANK_TEMP_CTRL.CURR_SP | Real | %DB42.DBD1922 | CURRENT RAMP SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_PID_FAN_SPD_OUT_3 | Real | %DB40.DBD60 | STOKER PID AIR FAN SPEED OUTPUT 3 | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.STOKER_1_MAN_ST | Bool | %DB1.DBX5.1 | CP3 STOKER 1 TRAVERSE MANUAL START SELECT (SCADA) | Cyclic in operation | 1 s
IDB CP13 FILT DIS FAN DP.Status | Int | %DB551.DBW2 | Motor Status | Cyclic in operation | 1 s
DB LV GEN POWER METER.M5_PAC3200.V3_V1 | Real | %DB201.DBD20 | VOLTS PHASE 3 TO PHASE 1 (VOLTS) | Cyclic in operation | 1 s
DB SETPOINTS.PID.BICARB_FEED.GAIN | Real | %DB40.DBD1780 | P TERM (GAIN) | Cyclic in operation | 1 s
DB SAFETY.RECV.CP7_2LSZ01 | Bool | %DB44.DBX4.1 | BOILER PANEL CP7 BOILER HI HI WATER LEVEL (1=HEALTHY) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD5.CP18_1TT08 | Bool | %DB11.DBX16.7 | CP18 PRIMARY AIR DUCT AIR TEMPERATURE PROBE | Cyclic in operation | 1 s
IDB ID FAN A PBUS.Recv.StatusWord | Word | %DB511.DBW24 | Status Word | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4FT01.HYST | Real | %DB41.DBD1968 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_PRDS_CTRL.RAMP_RATE | Real | %DB40.DBD1172 | RAMP TO SETPOINT RATE | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP17_4TT01 | Real | %DB42.DBD236 | CP17 DEAERATOR WATER TEMPERATURE PROBE (4-20mA = xx ºC) | Cyclic in operation | 1 s
5CV01_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BOILER.CP7_PLANT_PUMP_STOP_SP | Real | %DB40.DBD644 | TREATED WATER TANK WATER PRESSURE TO STOP PLANT PUMP SETPOINT (Bar) | Cyclic in operation | 1 s
DB LV GEN POWER METER.M5_PAC3200.PFtot | Real | %DB201.DBD100 | TOTAL POWER FACTOR | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_PID_FLOW_OUT_4 | Real | %DB40.DBD104 | STOKER PID AIR FLOW OUTPUT 4 | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2MTR05_REV | Bool | %DB45.DBX12.1 | CP8 ECONOMISER SOOTBLOWER 1 MOTOR RUN REVERSE | Cyclic in operation | 1 s
DB PROCESS VALUES.EMISSIONS.TEMP_Deg_C | Real | %DB42.DBD860 | STACK TEMPERATURE (Deg C) | Continuous | 1 s
DB LV GEN POWER METER.KVA3 | Real | %DB201.DBD124 | APPARANT POWER PHASE 3 (KVA) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_1_PID_FLOW_OUT_4 | Real | %DB40.DBD460 | GRATE PID AIR FLOW OUTPUT 4 | Cyclic in operation | 1 s
IDB CP3 DISTRIB SCREW.Status.StatusWord | Int | %DB110.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2MTR01_REV | Bool | %DB45.DBX10.1 | CP8 SUPERHEATER SOOTBLOWER 1 MOTOR RUN REVERSE | Cyclic in operation | 1 s
IDB PRIM AIR FAN PBUS.Status.Load | Real | %DB513.DBD50 | Drive Load in Percentage (%) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_1_SPD_MIN | Real | %DB40.DBD480 | GRATE MINIMUM SPEED | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_8PT01.LOLO | Real | %DB41.DBD1676 | LOW LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_SPD_MIN | Real | %DB40.DBD340 | STOKER MINIMUM SPEED | Cyclic in operation | 1 s
IDB CP12 ALTERNTR COOLER.Rem_Cmds.RemoteCtrl | Bool | %DB173.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT03.HIHI | Real | %DB41.DBD2368 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD2.CP7_7PLT07 | Bool | %DB11.DBX10.5 | CP7 COOLING CIRCULATION WATER FLOW PRESSURE | Cyclic in operation | 1 s
IDB ST HYD PUMP 2 PBUS.Status.ErrorCode | Int | %DB501.DBW46 | Last Trip Code | Cyclic in operation | 1 s
STOP 1MTR01 | Timer | %T43 | CP2 PUSH FLOOR HYDRAULIC POWER PACK STOP DELAY TIMER | Cyclic in operation | 1 s
DB SETPOINTS.PID.STOKER_1.MANUAL_VAL | Real | %DB40.DBD1454 | PID OUTPUT IN MANUAL (MAN) | Cyclic in operation | 1 s
IDB CP13 UREA SKID SYS.Status.StatusWord | Int | %DB148.DBW22 | Motor Status Word | Cyclic in operation | 1 s
PRIM_AIR_FAN_SHOW | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
IDB CP22 EDDY CURR SEP.Rem_Cmds.RunFwd | Bool | %DB104.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB ALARMS TO SCADA.COOLERS.COOLER4.WORD1 | Int | %DB12.DBW142 | COOLER 4 ALARMS - WORD 1 | Continuous | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP18_1TT04 | Real | %DB42.DBD300 | CP18 RESIDENCE CHAMBER TEMPERATURE PROBE 3 | Cyclic in operation | 1 s
DB ALARMS TO SCADA.SUPPLIES.WORD1 | Int | %DB12.DBW86 | POWER SUPPLY ALARMS - WORD 1 | Continuous | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_S2631 | Bool | %DB45.DBX24.4 | CP13 RACK 4 P.A.C. HOPPER LEVEL PROBE | Cyclic in operation | 1 s
IDB CP2 SCRAPER CHAIN DP.Status | Int | %DB522.DBW2 | Motor Status | Cyclic in operation | 1 s
DB SETPOINTS.PID.SECOND_FAN.OP_OFFSET | Real | %DB40.DBD1430 | OUTPUT OFFSET (LMN_OFF) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 5.SEND.GENERAL.START_ADIABATIC | Bool | %DB165.DBX71.0 | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.SECOND_AIR_FAN.O2_PID_LOAD_5 | Real | %DB40.DBD748 | SECONDARY AIR FAN PID CONTROLLER LOAD POINT 5 | Cyclic in operation | 1 s
IDB CP3 STOKER HYD PMP 2.Status.StatusWord | Int | %DB113.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.START.TIMERS.DISTRIB_SCREW_1MTR10 | S5Time | %DB30.DBW80 | HOPPER DISTRIBUTION SCREW | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.BURNER.CP18_1SW44 | Bool | %DB45.DBX15.0 | CP18 GRATE 2 FORWARD SWITCH 1 | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BURNER.SECOND_FAN_CTRL_MD | Bool | %DB1.DBX38.6 | CP13 SECONDARY AIR FAN CONTROL MODE (0 = SINGLE SP, 1 = CURVE) | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_PUMP.OP_SCALE | Real | %DB40.DBD1886 | OUTPUT SCALE FACTOR (LMN_FAC) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD5.CP17_2TT06 | Bool | %DB11.DBX16.0 | CP17 STEAM BLEED TO FEED WATER TANK TEMPERATURE (4-20mA = xx ºC) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.HIHI.WORD4.CP17_4PT01 | Bool | %DB11.DBX28.6 | CP17 DEAERATOR PRESSURE TRANSDUCER (4-20mA = xx Bar) | Cyclic in operation | 1 s
Bicarb_Load_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SEND/RECV COOLER 6.RECV.GENERAL.FANS_STATUS | Int | %DB166.DBW4 | COOLER FANS STATUS | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.SOOTHING_MD | Bool | %DB1.DBX20.5 | CP8 SOOTHING CYCLE MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
IDB CP2 SCRAPER CHAIN.Rem_Cmds.RemoteCtrl | Bool | %DB101.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_3TI01a.HIHI | Real | %DB41.DBD992 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP17_2TT06 | Real | %DB42.DBD256 | CP17 STEAM BLEED TO FEED WATER TANK TEMPERATURE (4-20mA = xx ºC) | Cyclic in operation | 1 s
DB LV GEN POWER METER.KWh | Real | %DB201.DBD164 | ACTIVE ENERGY USAGE (KWh) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FEED_LINE.CP18_1SW12 | Bool | %DB45.DBX7.4 | CP18 STOKER 2 FORWARD PROXIMITY SWITCH | Cyclic in operation | 1 s
IDB PRIM AIR FAN PBUS.Status.ErrorCode | Int | %DB513.DBW54 | Last Trip Code | Cyclic in operation | 1 s
DB SETPOINTS.PID.BOILER_FEED_WATER_VLV.SP | Real | %DB40.DBD1214 | INTERNAL SETPOINT | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_8LO01.LO | Real | %DB41.DBD936 | LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_PID_LAMBDA_MAX | Real | %DB40.DBD112 | STOKER PID AIR LAMBDA MAXIMUM SCALING VALUE | Cyclic in operation | 1 s
1MTR09_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BURNER.BRN_ALL_TEMP_IN_USE | Bool | %DB1.DBX36.4 | RESIDANCE CHAMBER TEMPERATURE ALL PROBES 1TT02/03/04 VALUES IN USE | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP2_1TS06 | Real | %DB42.DBD8 | CP2 SCRAPER CHAIN CONVEYOR MOTOR THERMISTOR (PT100 = 0-150 ºC) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 5.RECV.PROCESS_VALUES.COOL_FAN_ACT_SPD | Real | %DB165.DBD26 | COOLING FANS ACTUAL SPEED | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.BICARB_FEED_HCL.PID_ACTV | Bool | %DB42.DBX2160.1 | PID CONTROLLER ACTIVE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TT07.LOLO | Real | %DB41.DBD3276 | LOW LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MODE_STATUS.EXEC_OPMODE_2_STAT | Int | %DB30.DBW36 | EXECUTIVE OVERRIDE MODE 2 STATUS (0=NOT SEL, 1=REQ, 2=REQ & ACHIEVED) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.ECONOM_2_RET | Bool | %DB1.DBX20.1 | CP8 ECONOMISER SOOTBLOWER 2 MANUAL RETRACT SELECT (SCADA) | Cyclic in operation | 1 s
DB LV GEN POWER METER.KWtot | Real | %DB201.DBD156 | TOTAL ACTIVE POWER (KW) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.GENERAL.ALARM_MUTE | Bool | %DB1.DBX0.2 | CP4 MUTE ALARM SOUNDER (FROM SCADA) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2MTR04_REV | Bool | %DB45.DBX11.5 | CP8 BOILER SOOTBLOWER 2 MOTOR RUN REVERSE | Cyclic in operation | 1 s
IDB CP2 SCRAPER CHAIN.Status.StatusWord | Int | %DB101.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2PSZ02.HI | Real | %DB41.DBD2788 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.PID.BOILER_FEED_WATER_VLV.MAN_AUTO | Bool | %DB40.DBX1250.0 | PID MANUAL/AUTO MODE (1=MANUAL) (MAN_ON) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4LC02.HYST | Real | %DB41.DBD1840 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TT02.LOLO | Real | %DB41.DBD3052 | LOW LOW ALARM SETPOINT | Cyclic in operation | 1 s
IDB CP13 RS LOAD BELLOW.Status.StatusWord | Int | %DB138.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.SOOTBLOWERS.SP67 | Int | %DB1.DBW260 | <No Value> | Cyclic in operation | 1 s
DB SCADA DATA.DWORD_DATA.SD_ACTUAL_DOS | Real | %DB45.DBD112 | ACTUAL DOSING FROM SULPHUR DOSING PLANT | Cyclic in operation | 1 s
DB SETPOINTS.PID.HI_PRESS_CTRL_STEAM.GAIN | Real | %DB40.DBD1550 | P TERM (GAIN) | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_18 | Bool | %DB2.DBX296.1 | Profibus Node | Cyclic in operation | 1 s
DB ALARMS TO SCADA.PROCESS.WORD9 | Int | %DB12.DBW120 | PROCESS ALARMS - WORD 9 | Continuous | 1 s
DB SEND/RECV COOLER 5.RECV.PROCESS_VALUES.CIRC_WATER_OUT_TEMP | Real | %DB165.DBD22 | CIRCULATION WATER OUTLET TEMPERATURE | Cyclic in operation | 1 s
S2_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SEND/RECV COOLER 4.SEND.GENERAL.REMOTE_RUN | Bool | %DB164.DBX70.7 | 0 = STOP / 1 = RUN | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_8LO01.HYST | Real | %DB41.DBD944 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP7_7PLT07.LO | Real | %DB41.DBD680 | LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_8IN02.HYST | Real | %DB41.DBD1232 | ALARM HISTERESYS | Cyclic in operation | 1 s
IDB CP3 ASH SCRAPER CONV.Status.StatusWord | Int | %DB111.DBW22 | Motor Status Word | Cyclic in operation | 1 s
SecondFanPID_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
8MTR02_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_3TI01c.HYST | Real | %DB41.DBD1136 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB ALARMS.ESTOPS.WORD2.CP17_4LC01 | Bool | %DB11.DBX80.7 | DEAERATOR PANEL CP17 DEAERATOR LO LO LEVEL TRIP | Cyclic in operation | 1 s
DB ALARMS TO SCADA.PROCESS.WORD10 | Int | %DB12.DBW122 | PROCESS ALARMS - WORD 10 | Continuous | 1 s
DB SAFETY.RECV.CP18_1PT02 | Bool | %DB44.DBX5.0 | BURNER PANEL CP18 HI HI COMBUSTION CHAMBER PRESSURE TRIP (1=HEALTHY) | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.BURNER.ASH_SCRAPER_RUNON | Int | %DB40.DBW960 | ASH SCRAPER CONVEYOR RUN ON TIME (SEC) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.START.BITS.BICARB_SYS | Bool | %DB30.DBX148.3 | SODIUM BICARBONATE SILO AND FEED SYSTEM | Cyclic in operation | 1 s
DB SEND/RECV COOLER 6.RECV.PROCESS_VALUES.COOL_FAN_ACT_SPD | Real | %DB166.DBD26 | COOLING FANS ACTUAL SPEED | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_S2461 | Bool | %DB45.DBX23.0 | CP13 RACK 4 RESIDUE SILO LOW LEVEL SIDE ENTRY LEVEL PROBE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_2TT06.LOLO | Real | %DB41.DBD2060 | LOW LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB SEND/RECV COOLER 6.SEND.SETPOINTS.FANS_SPEED_MANUAL | Real | %DB166.DBD110 | FANS SPEED FOR REMOTE MANUAL MODE | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_S2571 | Bool | %DB45.DBX23.7 | CP13 RACK 4 BICARB SILO LOW LEVEL SIDE ENTRY LEVEL PROBE | Cyclic in operation | 1 s
MODE 5 Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.PRIM_FAN.PID_ACTV | Bool | %DB42.DBX1680.1 | PID CONTROLLER ACTIVE | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP13R4_3TI01c | Real | %DB42.DBD140 | CP13 RACK 4 FILTER 2 INLET AIR TEMPERATURE (4..20mA = -50 - +300ºC) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.BURNER.CP18_1SW42 | Bool | %DB45.DBX14.4 | CP18 GRATE 1 FORWARD SWITCH 2 | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT04.HI | Real | %DB41.DBD2404 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD5.CP18_1PT01 | Bool | %DB11.DBX17.4 | CP18 MOVING GRATE PRESSURE TRANSMITTER 1 | Cyclic in operation | 1 s
DB SEND/RECV COOLER 4.SEND.TIMES.MIN_RUN_TIME | Time | %DB164.DBD214 | COOLER MINIMUM RUN TIME | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.BICARB_FEED_HCL.OUTPUT | Real | %DB42.DBD2178 | OUTPUT VALUE | Cyclic in operation | 1 s
IDB GR HYD PUMP 1 PBUS.Send.ControlWord | Word | %DB503.DBW8 | Control Word | Cyclic in operation | 1 s
IDB CP13 SECON AIR FAN.Rem_Cmds.RunFwd | Bool | %DB147.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.WOOD_FEED.STK_2_PID_SEL_PV | Int | %DB1.DBW186 | CP3 STOKER 2 FEED PID (0 = STANDARD, 1 = LAMBDA, 2 = FAN SPEED, 3 = AIR FLOW) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2PT01.HI | Real | %DB41.DBD2692 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_SB1a | Bool | %DB45.DBX21.1 | CP13 RACK 4 FILTER 1 INLET VALVE B OPENED | Cyclic in operation | 1 s
DB SEND/RECV COOLER 5.SEND.SETPOINTS.FANS_SPEED_MANUAL | Real | %DB165.DBD110 | FANS SPEED FOR REMOTE MANUAL MODE | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD4.CP17_2PT06 | Bool | %DB11.DBX14.5 | CP17 FEEDWATER TANK STEAM BLEED PRESSURE TRANSDUCER (4-20mA = 0-55 Bar) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.ECONOM_3_EXT | Bool | %DB1.DBX20.3 | CP8 ECONOMISER SOOTBLOWER 3 MANUAL EXTEND SELECT (SCADA) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_PID_FAN_SPD_4 | Real | %DB40.DBD148 | STOKER PID AIR FAN SPEED POINT 4 | Cyclic in operation | 1 s
Brn_Load_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
1CV04_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARMS.SYSTEM.WORD1.CP4_CPU_HEALTHY | Bool | %DB11.DBX1.1 | CP4 PILZ CPU HEALTHY (192.168.2.104) | Cyclic in operation | 1 s
IDB CP3 GRATE HYD PMP 1.Rem_Cmds.RunFwd | Bool | %DB115.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP7_U75.HYST | Real | %DB41.DBD592 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB SETPOINTS.PID.RECIRC_FAN.OP_OFFSET | Real | %DB40.DBD1338 | OUTPUT OFFSET (LMN_OFF) | Cyclic in operation | 1 s
DB ALARMS TO SCADA.COOLERS.COOLER2.WORD2 | Int | %DB12.DBW136 | COOLER 2 ALARMS - WORD 2 | Continuous | 1 s
CP7 4PU02 SELECTED | Bool | %M142.2 | CP7 STANDBY BOILER FEED PUMP DUTY SELECTED | Cyclic in operation | 1 s
STOP 1MTR03 | Timer | %T42 | CP2 SCRAPER CHAIN CONVEYOR STOP DELAY TIMER | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_U113_DP.HYST | Real | %DB41.DBD880 | ALARM HISTERESYS | Cyclic in operation | 1 s
IDB CP13 PAC AGITATOR DP.Load | Real | %DB555.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4TT01.HI | Real | %DB41.DBD1892 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.PID.ID_FAN.OP_SCALE | Real | %DB40.DBD1288 | OUTPUT SCALE FACTOR (LMN_FAC) | Cyclic in operation | 1 s
IDB CP7 LIFT PUMP 1.Rem_Cmds.RemoteCtrl | Bool | %DB182.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.BURNER.GRATE_RUNON_TIME_MODE8 | Int | %DB40.DBW948 | GRATES RUN-ON TIME IN AUTO MODE 8 - BURN OFF (MIN) | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.OIL_BURNER.PID_ACTV | Bool | %DB42.DBX1890.1 | PID CONTROLLER ACTIVE | Cyclic in operation | 1 s
IDB CP3 GRATE HYD PMP 1.Status.Running | Bool | %DB115.DBX20.7 | Motor Running | Cyclic in operation | 1 s
DB SETPOINTS.PID.STOKER_1.OP_MAX | Real | %DB40.DBD1464 | OUTPUT MAX VALUE (LMN_HLM) | Cyclic in operation | 1 s
DB LV GRID POWER METER.M4_PAC3200.V1_V2 | Real | %DB200.DBD12 | VOLTS PHASE 1 TO PHASE 2 (VOLTS) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_2_PID_FLOW_OUT_1 | Real | %DB40.DBD508 | GRATE PID AIR FLOW OUTPUT 1 | Cyclic in operation | 1 s
3MTR04b_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.FILTER.RS_PULSE_CTRL_STAT | Int | %DB1.DBW228 | RESIDUE SILO PULSE CONTROLLER STATUS | Cyclic in operation | 1 s
MODE 7 Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_PRDS_CTRL.INTEGRAL | Int | %DB40.DBW1186 | I TERM (TI) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.SLIDE_VLV_CLS | Bool | %DB1.DBX4.7 | CP3 SLIDE VALVE MANUAL CLOSE SELECT (SCADA) | Cyclic in operation | 1 s
DB SETPOINTS.PID.BOILER_FEED_WATER_VLV.INTEGRAL | Int | %DB40.DBW1232 | I TERM (TI) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.PUSH_FLOOR.CP2_1SW21_MAX | Bool | %DB45.DBX2.6 | CP2 PUSH FLOOR LADDER No 2 MAXIMUM PROXIMITY | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.START.TIMERS.LEV_SCREW_1MTR02 | S5Time | %DB30.DBW86 | LEVELLING SCREW | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BOILER.TURBINE_PWR_OPEN_5CV01 | Real | %DB40.DBD660 | TURBINE POWER TO OPEN STEAM BLEED VALVE (KW) | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.WOOD_FEED.ED_SEP_RUN_ON_TIME | Int | %DB40.DBW902 | EDDY CURRENT SEPARATOR RUN ON TIME (x10 SEC) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.BOILER_1_EXT | Bool | %DB1.DBX18.7 | CP8 BOILER SOOTBLOWER 1 MANUAL EXTEND SELECT (SCADA) | Cyclic in operation | 1 s
DB SAFETY.RECV.CP19_2PSZ01 | Bool | %DB44.DBX4.2 | BOILER PANEL CP19 HI HI STEAM DRUM PRESSURE TRIP (1=HEALTHY) | Cyclic in operation | 1 s
IDB CP7 PLANT PUMP 2.Status.StatusWord | Int | %DB188.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.TURBINE.STEAM_TEMP | Real | %DB42.DBD1124 | TURBINE LIVE STEAM TEMPERATURE | Cyclic in operation | 1 s
DB SEND/RECV COOLER 1.SEND.GENERAL.START_COOLER | Bool | %DB161.DBX70.5 | <No Value> | Cyclic in operation | 1 s
IDB ST HYD PUMP 3 PBUS.Control.RefSpeed | Real | %DB502.DBD32 | Drive Speed Reference in Percentage (%) | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD2.SUSP_WOOD_FEED_WID | Bool | %DB11.DBX107.5 | SUSPEND WOOD FEED DUE TO WID TIME LIMIT EXCEEDED ALARM | Cyclic in operation | 1 s
IDB CP3 EN-MASSE CHN CON.Rem_Cmds.RunFwd | Bool | %DB106.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
IDB CP13 BS AGITATOR.Status.StatusWord | Int | %DB139.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP18_1TT01 | Real | %DB42.DBD288 | CP18 MOVING GRATE TEMPERATURE (0-1500 ºC) | Cyclic in operation | 1 s
DB SETPOINTS.PID.ID_FAN.OP_OFFSET | Real | %DB40.DBD1292 | OUTPUT OFFSET (LMN_OFF) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT08.HYST | Real | %DB41.DBD2288 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP2_1TS05.HYST | Real | %DB41.DBD48 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.BRN_PRESS_COMP | Real | %DB40.DBD392 | BURNER COMBUSTION ZONE AIR PRESSURE SENSORS COMPARISON WINDOW (mbar) | Cyclic in operation | 1 s
STRT 1GR01 | Timer | %T51 | CP22 EDDY CURRENT SEPARATOR START DELAY TIMER | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_S252 | Bool | %DB45.DBX23.1 | CP13 RACK 4 RESIDUE SILO INCLINED DISCHARGE SCREW PRESSURE SWITCH | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_1_PID_FLOW_OUT_1 | Real | %DB40.DBD448 | GRATE PID AIR FLOW OUTPUT 1 | Cyclic in operation | 1 s
CP8 SOOTHING CYCLE | Bool | %M88.0 | CP8 SOOTHING CYCLE RUNNING | Cyclic in operation | 1 s
SCADA MAIN ES RST | Bool | %M41.0 | SCADA MAIN ESTOP RESET | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.PRIM_FAN.RAMP_ACTV | Bool | %DB42.DBX1680.0 | RAMP ACTIVE | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD1.CP22_ED_SEP_BLOCK | Bool | %DB11.DBX105.5 | CP3 EDDY CURRENT SEPARATOR DISCHARGE BLOCKED ALARM | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_PID_FAN_SPD_OUT_5 | Real | %DB40.DBD68 | STOKER PID AIR FAN SPEED OUTPUT 5 | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.FILTER.BS_HOPPER_VIB_ON | Int | %DB40.DBW992 | BICARB HOPPER VIBRATOR ON TIME (SEC) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TT05.HIHI | Real | %DB41.DBD3136 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.HI.WORD5 | Int | %DB12.DBW44 | HIGH ALARMS - WORD 5 | Continuous | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.SLIDE_VLV_MD | Bool | %DB1.DBX4.5 | CP3 SLIDE VALVE MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2PT01.HYST | Real | %DB41.DBD2704 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB SETPOINTS.PID.PRESS_CTRL_STEAM_OUT.OP_MIN | Real | %DB40.DBD1652 | OUTPUT MIN VALUE (LMN_LLM) | Cyclic in operation | 1 s
DB MV TURB POWER METER.KVA1 | Real | %DB202.DBD116 | APPARANT POWER PHASE 1 (KVA) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.STK_3_PID_MTHD_2_SEL | Bool | %DB1.DBX8.3 | STOKER 3 PID CONTROLLER METHOD 2 SELECTED | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1PT01.HI | Real | %DB41.DBD2436 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2SW09 | Bool | %DB45.DBX12.2 | CP8 ECONOMISER SOOTBLOWER 1 RETRACTED PROXIMITY SWITCH | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_37 | Bool | %DB2.DBX298.4 | Profibus Node | Cyclic in operation | 1 s
MODE 8 Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_8LT04.HYST | Real | %DB41.DBD1648 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.FILTER.BIC_SILO_VIBRATOR_MD | Bool | %DB1.DBX31.6 | BICARB SILO VIBRATOR MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 3.RECV.PROCESS_VALUES.COOL_FAN_ACT_SPD | Real | %DB163.DBD26 | COOLING FANS ACTUAL SPEED | Cyclic in operation | 1 s
DB SEND/RECV COOLER 1.SEND.GENERAL.REMOTE_RUN | Bool | %DB161.DBX70.7 | 0 = STOP / 1 = RUN | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.STOP.TIMERS.ID_FANS | S5Time | %DB30.DBW190 | MAIN FILTER FANS | Cyclic in operation | 1 s
AIR FANs OK FOR AUTO ST | Bool | %M132.0 | RECIRCULATION FAN READY / AVAILABLE FOR SYSTEM AUTO START | Cyclic in operation | 1 s
DB SEND/RECV COOLER 6.SEND.GENERAL.START_COOLER | Bool | %DB166.DBX70.5 | <No Value> | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TT01.HYST | Real | %DB41.DBD3024 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB SETPOINTS.PID.PRIM_FAN.RAMP_EN | Bool | %DB40.DBX1388.2 | RAMP ENABLED (1=ENABLED) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2MTR05_FWD | Bool | %DB45.DBX12.0 | CP8 ECONOMISER SOOTBLOWER 1 MOTOR RUN FORWARD | Cyclic in operation | 1 s
DB ALARMS TO SCADA.LOCAL_ISOL.WORD1 | Int | %DB12.DBW96 | AC MOTOR LOCAL ISOLATOR ALARMS - WORD 1 | Continuous | 1 s
8MTR03_HCL_PID_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_3LO01.HIHI | Real | %DB41.DBD896 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
IDB CP2 SCRAPER CHAIN.Rem_Cmds.RunFwd | Bool | %DB101.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
IDB CP7 LP DOSING PMP2.Rem_Cmds.RunFwd | Bool | %DB186.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.SOOTBLOWERS.BOILER_2_NB_2 | Int | %DB40.DBW1032 | BOILER SOOTBLOWER 2 NUMBER 2 | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.HI_TEMP_CTRL_STEAM.OUTPUT | Real | %DB42.DBD1788 | OUTPUT VALUE | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP13R4_3LO01 | Real | %DB42.DBD112 | CP13 RACK 4 RESIDUE SILO LOAD CELL WEIGHT (4..20mA = xx Tones) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_S2551 | Bool | %DB45.DBX22.2 | CP13 RACK 4 BICARB SILO MAINTENANCE BUTTERFLY VALVE OPENED | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.LEV_AUG_ROT_SENS_OFF | Bool | %DB1.DBX4.0 | CP2 LEVELLING AUGER ROTATION SENSOR DISABLE (SCADA) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.START.BITS.PUSH_FLOOR_1HP01 | Bool | %DB30.DBX74.6 | PUSH FLOOR TRAVEL SOLENOIDS | Cyclic in operation | 1 s
DB SAFETY.RECV.SILOS_ESR_OK | Bool | %DB44.DBX0.2 | Filter Silos Emergency Stop Healthy (bicarb load and unload to/from silos only) | Cyclic in operation | 1 s
IDB CP3 EN-MASSE CHN DP.Load | Real | %DB530.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_1_PID_FLOW_5 | Real | %DB40.DBD444 | GRATE PID AIR FLOW POINT 5 | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_OBSTR_PRESET | Real | %DB40.DBD20 | STOKER 1 OBSTRUCTION ALARM COUNTER PRESET | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_2_PID_FLOW_3 | Real | %DB40.DBD496 | GRATE PID AIR FLOW POINT 3 | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2SW13 | Bool | %DB45.DBX13.2 | CP8 ECONOMISER SOOTBLOWER 3 RETRACTED PROXIMITY SWITCH | Cyclic in operation | 1 s
DB SAFETY.SEND.FWP2_4PU02_RUNNING | Bool | %DB44.DBX81.2 | 4PU02 Feed Water Pump No 2 Running (1=Running) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4PT01.HI | Real | %DB41.DBD1732 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.LOLO.WORD2 | Int | %DB12.DBW66 | LOW LOW ALARMS - WORD 2 | Continuous | 1 s
DB MISCELLANEOUS.INTEGERS.SOOTBLOWERS.SP68 | Int | %DB1.DBW262 | <No Value> | Cyclic in operation | 1 s
DB SAFETY.SEND.IDF2_3FA02_RUNNING | Bool | %DB44.DBX82.4 | 3FA02 ID Fan No.2 Running (PIW520 / DB512.DBX25.1) - 1=Running | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BOILER.FEEDWTR_VLV_PID_MD | Bool | %DB1.DBX23.0 | CP17 FEEDWATER VALVE PID MODE SELECT (0 = SINGLE, 1 = MULTIPLE) (SCADA) | Cyclic in operation | 1 s
IDB CP13 FILTER SCREW A.Rem_Cmds.RunFwd | Bool | %DB126.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD5.CP18_1TT02 | Bool | %DB11.DBX17.1 | CP18 RESIDENCE CHAMBER TEMPERATURE PROBE 1 | Cyclic in operation | 1 s
IDB ID FAN B PBUS.Status.Load | Real | %DB512.DBD50 | Drive Load in Percentage (%) | Cyclic in operation | 1 s
DB PROCESS VALUES.EMISSIONS.TOC_Mg_m3 | Real | %DB42.DBD824 | TOTAL ORGANIC COMPOUNDS TOC (Mg/m3) | Continuous | 1 s
IDB CP7 SB FEED PUMP.Status.StatusWord | Int | %DB181.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.HI.WORD4.CP17_4TT01 | Bool | %DB11.DBX43.3 | CP17 DEAERATOR WATER TEMPERATURE PROBE (4-20mA = xx ºC) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.STOP.TIMERS.BICARB_SYS | S5Time | %DB30.DBW188 | SODIUM BICARBONATE SILO AND FEED SYSTEM | Cyclic in operation | 1 s
DB SEND/RECV COOLER 1.RECV.ADIABATIC.STATUS | Int | %DB161.DBW30 | ADIABATIC SYSTEM STATUS | Cyclic in operation | 1 s
DB MV TURB POWER METER.M6_PAC3200.PF2 | Real | %DB202.DBD76 | POWER FACTOR PHASE 2 | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.POWER.SITE_IMPORT_EXPORT_KW | DInt | %DB42.DBD1208 | SITE IMPORT / EXPORT POWER (kW) | Cyclic in operation | 1 s
IDB SCND AIR FAN PBUS.Status.ActualSpeed | Real | %DB514.DBD46 | Actual Speed in Percentage (%) | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.SECOND_FAN.OUTPUT | Real | %DB42.DBD1728 | OUTPUT VALUE | Cyclic in operation | 1 s
IDB GR HYD PUMP 1 PBUS.Recv.StatusWord | Word | %DB503.DBW20 | Status Word | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.OPN_SHT.WORD5 | Int | %DB12.DBW16 | OPEN/SHORT CIRCUIT ALARMS - WORD 5 | Continuous | 1 s
DB ALARMS.ANALOGUE.HI.WORD6.CP19_2LT01 | Bool | %DB11.DBX46.3 | CP19 DP CELL WATER LEVEL | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MODE_STATUS.EXEC_OPMODE_3_STAT | Int | %DB30.DBW38 | EXECUTIVE OVERRIDE MODE 3 STATUS (0=NOT SEL, 1=REQ, 2=REQ & ACHIEVED) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4PLT03.HIHI | Real | %DB41.DBD1984 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TT05.HI | Real | %DB41.DBD3140 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.LO.WORD7 | Int | %DB12.DBW62 | LOW ALARMS - WORD 7 | Continuous | 1 s
DB PROCESS VALUES.EMISSIONS.HCL_Mg_m3 | Real | %DB42.DBD828 | HYDROGEN CHLORIDES Hcl (Mg/m3) | Continuous | 1 s
DB PROCESS VALUES.PID.ID_FAN.PID_ACTV | Bool | %DB42.DBX1620.1 | PID CONTROLLER ACTIVE | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_PUMP.OP_MIN | Real | %DB40.DBD1882 | OUTPUT MIN VALUE (LMN_LLM) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.FILTER.RES_SILO_BELLOWS_LOWER | Bool | %DB1.DBX29.6 | RESIDUE SILO BELLOWS MANUAL LOWER SELECT (SCADA) | Cyclic in operation | 1 s
CP7 8PU02 SELECTED | Bool | %M146.2 | CP7 STANDBY LIFT PUMP DUTY SELECTED | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.FILTER.BS_FILL_VLV_STAT | Int | %DB1.DBW242 | BICARB SILO FILL VALVE STATUS | Cyclic in operation | 1 s
DB ALARMS TO SCADA.PROFIBUS.WORD3 | Int | %DB12.DBW6 | PROFIBUS ALARMS - WORD 3 | Continuous | 1 s
DB SYSTEM CONTROL.GENERAL.MAIN_CTRL.OIL_BURNER_START | Bool | %DB30.DBX1.4 | START OIL BURNER (FROM SCADA) | Cyclic in operation | 1 s
3MTR02_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
IDB CP13 RS LOAD BELL DP.Load | Real | %DB558.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
IDB CP7 MN FEED PUMP.Status.StatusWord | Int | %DB180.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.TURBINE_2.VOLT_L1_L2 | Real | %DB42.DBD1412 | VOLTAGE L1-L2 | Cyclic in operation | 1 s
3UR01_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BURNER.BRN_TEMP_1TT02_IN_USE | Bool | %DB1.DBX36.5 | RESIDANCE CHAMBER TEMPERATURE PROBE 1TT02 VALUE IN USE | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.FILTER.FILT2_IN_VLV_STAT | Int | %DB1.DBW226 | FILTER 2 INLET VALVE STATUS | Cyclic in operation | 1 s
DB LV GEN POWER METER.M5_PAC3200.PF3 | Real | %DB201.DBD80 | POWER FACTOR PHASE 3 | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_TEMP_CTRL.OP_OFFSET | Real | %DB40.DBD1752 | OUTPUT OFFSET (LMN_OFF) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD2.CP7_7TT07 | Bool | %DB11.DBX10.3 | CP7 COOLING CIRCULATION WATER FLOW TEMPERATURE | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_SPD_OFFSET | Real | %DB40.DBD120 | STOKER SPEED OFFSET | Cyclic in operation | 1 s
DB SEND/RECV COOLER 2.RECV.PROCESS_VALUES.CIRC_WATER_OUT_TEMP | Real | %DB162.DBD22 | CIRCULATION WATER OUTLET TEMPERATURE | Cyclic in operation | 1 s
3MTR06_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_TEMP_CTRL.RAMP_RATE | Real | %DB40.DBD1724 | RAMP TO SETPOINT RATE | Cyclic in operation | 1 s
8MTR01_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
IDB PRIM AIR FAN PBUS.Control.RefSpeed | Real | %DB513.DBD40 | Drive Speed Reference in Percentage (%) | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.BURNER.BRN_VACUUM_AVG_VALUE | Real | %DB42.DBD1240 | BURNER VACUUM SENSOR AVERAGED VALUE | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BOILER.CP6_WTR_TREAT_STOP_SP | Real | %DB40.DBD652 | TREATED WATER TANK WATER LEVEL TO STOP WATER TREATMENT SETPOINT (%) | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.BURNER.GRT_1_TRAV_MAX_TIMEOUT | Int | %DB40.DBW952 | GRATE 1 TRAVERSE MAXIMUM TIMEOUT TIME (SEC) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BOILER.CP7_LIFT_PUMP_STOP_SP | Real | %DB40.DBD636 | FEED WATER TANK WATER LEVEL TO STOP LIFT PUMP SETPOINT (%) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.PUSH_FLOOR.CP2_LAD_3_INSERV | Bool | %DB1.DBX2.6 | CP2 PUSH FLOOR LADDER 3 IN SERVICE | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.BURNER.GRT_1_TRAV_MIN_TIMEOUT | Int | %DB40.DBW966 | GRATE 1 TRAVERSE MINIMUM TIMEOUT TIME (SEC) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.GENERAL.ALL_EQUIP_AUTO | Bool | %DB30.DBX70.2 | ALL FEED LINE EQUIPMENT AUTO | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TSZ01.HYST | Real | %DB41.DBD2640 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB SETPOINTS.PID.STOKER_1.MAN_AUTO | Bool | %DB40.DBX1480.0 | PID MANUAL/AUTO MODE (1=MANUAL) (MAN_ON) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 4.RECV.GENERAL.WATCHDOG | Bool | %DB164.DBX0.0 | <No Value> | Cyclic in operation | 1 s
IDB CP13 RS INCLIN SCREW.Rem_Cmds.RemoteCtrl | Bool | %DB133.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.FILTER.FILT_TEMP_START_HTR | Real | %DB40.DBD688 | TEMPERATURE TO START FILTERS TRACE HEATING | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.OP_MODES.OP_MODE_2 | Bool | %DB30.DBX8.2 | SYSTEM IN OPERATION MODE 2 (PRE-FLIGHT) | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.BOILER.STEAM_SAT_TEMP | Real | %DB42.DBD1176 | STEAM SATURATED TEMPERATURE | Cyclic in operation | 1 s
IDB BICARB FEEDER PBUS.Control.RefSpeed | Real | %DB516.DBD32 | Drive Speed Reference in Percentage (%) | Cyclic in operation | 1 s
DB LV GRID POWER METER.M4_PAC3200.PFtot | Real | %DB200.DBD100 | TOTAL POWER FACTOR | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TT03.HYST | Real | %DB41.DBD3408 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB SETPOINTS.PID.PRIM_FAN.GAIN | Real | %DB40.DBD1366 | P TERM (GAIN) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_3LO01.HI | Real | %DB41.DBD900 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.STK_1_PID_MTHD_1_SEL | Bool | %DB1.DBX7.1 | STOKER 1 PID CONTROLLER METHOD 1 SELECTED | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_S257 | Bool | %DB45.DBX23.6 | CP13 RACK 4 BICARB SILO TOP ENTRY LEVEL PROBE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_8LT01.LOLO | Real | %DB41.DBD1612 | LOW LOW ALARM SETPOINT | Cyclic in operation | 1 s
IDB PRIM AIR FAN PBUS.Recv.StatusWord | Word | %DB513.DBW24 | Status Word | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT07.HI | Real | %DB41.DBD2244 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
FEED2_SHOW | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARMS.COOLERS.COOLER1.WORD2.COMMS_FAULT | Bool | %DB11.DBX132.0 | COMMUNICATION FAULT | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.HI.WORD6 | Int | %DB12.DBW46 | HIGH ALARMS - WORD 6 | Continuous | 1 s
DB SETPOINTS.TIMERS.BURNER.GRT_2_TRAV_INTERVAL | Int | %DB40.DBW954 | GRATE 2 TRAVERSE INTERVAL TIME (SEC) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.LO.WORD4.CP17_4LC02 | Bool | %DB11.DBX57.1 | CP17 DEAERATOR WATER LEVEL TRANSDUCER (4-20mA = 0-100%) | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK1.EXT_STEAM_PRESSURE | DInt | %DB400.DBD16 | EXTRACTION STEAM PRESSURE BAR (x100) | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.FILTER.FILT1_PULSE_CTRL_STAT | Int | %DB1.DBW220 | FILTER 1 PULSE CONTROLLER STATUS | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT01.HYST | Real | %DB41.DBD2320 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_PID_FLOW_4 | Real | %DB40.DBD84 | STOKER PID AIR FLOW POINT 4 | Cyclic in operation | 1 s
Display_Menu | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.BURNER.O2_PURGE_OFF_TIME | Int | %DB40.DBW972 | O2 METER PURGE OFF TIME (SEC) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.PUSH_FLOOR.CP2_24VDC | Bool | %DB45.DBX2.0 | CP2 24VDC POWER SUPPLY HEALTHY | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.WOOD_FEED.STK_1_TRAV_MIN_TIMEOUT | Int | %DB40.DBW906 | STOKER 1 TRAVERSE MINIMUM TIMEOUT TIME (SEC) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.BOILER.CP7_U13_MAN_OVR | Bool | %DB45.DBX28.0 | CP7 MAIN BOILER FEED PUMP IN MANUAL OVERRIDE MODE | Cyclic in operation | 1 s
DB SEND/RECV COOLER 4.SEND.GENERAL.START_ADIABATIC | Bool | %DB164.DBX71.0 | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.PID.TURBINE_STEAM_BLEED.MAN_AUTO | Bool | %DB40.DBX1940.0 | PID MANUAL/AUTO MODE (1=MANUAL) (MAN_ON) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FEED_LINE.CP3_1SW08 | Bool | %DB45.DBX8.3 | CP3 STOKER FUEL/FIRE DAMPER 1CV05 OPEN POSITION SENSOR | Cyclic in operation | 1 s
S3_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_2PT06.HIHI | Real | %DB41.DBD1696 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.SOOTBLOWERS.CYCLE_INTERVAL | Int | %DB40.DBW1008 | INTERVAL TIMER BETWEEN SOOTHING CYCLES (MIN) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT05.HYST | Real | %DB41.DBD2192 | ALARM HISTERESYS | Cyclic in operation | 1 s
IDB CP13 FILT SEAL A DP.Load | Real | %DB549.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2MTR06_FWD | Bool | %DB45.DBX12.4 | CP8 ECONOMISER SOOTBLOWER 2 MOTOR RUN FORWARD | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.START.BITS.ID_FANS | Bool | %DB30.DBX148.0 | MAIN FILTER FANS | Cyclic in operation | 1 s
DB SAFETY.SEND.TEMPERATURE_1TT07_OK | Bool | %DB44.DBX82.1 | 1TT07 High Temperature Flue Gas Recirculation (1=OK) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD6.CP19_2PT05 | Bool | %DB11.DBX19.3 | CP19 SOOTBLOWER STEAM PRESSURE | Cyclic in operation | 1 s
DB SEND/RECV COOLER 6.RECV.GENERAL.PUMP_STATUS | Int | %DB166.DBW2 | COOLER PUMP STATUS | Cyclic in operation | 1 s
DB SETPOINTS.PID.STOKER_3.MAN_AUTO | Bool | %DB40.DBX2032.0 | PID MANUAL/AUTO MODE (1=MANUAL) (MAN_ON) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MAIN_CTRL.FILTER_START | Bool | %DB30.DBX1.2 | START FILTER SYSTEM (FROM SCADA) | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.WOOD_FEED.STK_3_TRAV_MIN_TIMEOUT | Int | %DB40.DBW910 | STOKER 3 TRAVERSE MINIMUM TIMEOUT TIME (SEC) | Cyclic in operation | 1 s
STOP 1MTR02 | Timer | %T41 | CP2 LEVELLING SCREW STOP DELAY TIMER | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FEED_LINE.CP3_1SW05 | Bool | %DB45.DBX6.3 | CP3 SLIDE GATE VALVE CLOSED PROXIMITY SWITCH | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.WOOD_FEED.STOKER_TIMER_REMAIN | Int | %DB1.DBW180 | STOKER RUN-ON TIMER REMAINING TIME (MODE 7) | Cyclic in operation | 1 s
IDB CP22 EDDY CURR SEP.Status.StatusWord | Int | %DB104.DBW22 | Motor Status Word | Cyclic in operation | 1 s
1MTR18_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB PROCESS VALUES.EMISSIONS.H2O_PCT | Real | %DB42.DBD832 | WATER H2O (%) | Continuous | 1 s
IDB CP3 STOKER HYD PMP 1.Status.Running | Bool | %DB112.DBX20.7 | Motor Running | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.EQUIP_STATUS.RECIRC_FAN_IS_OFF | Bool | %DB30.DBX13.0 | RECIRCULATION AIR FAN IS OFF | Cyclic in operation | 1 s
DB SETPOINTS.PID.ID_FAN.GAIN | Real | %DB40.DBD1274 | P TERM (GAIN) | Cyclic in operation | 1 s
DB SETPOINTS.PID.HI_TEMP_CTRL_STEAM.SP | Real | %DB40.DBD1490 | INTERNAL SETPOINT | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD1.CP3_ENMASSE_TOP_BLOCK | Bool | %DB11.DBX105.7 | CP3 EN-MASSE CHAIN CONVEYOR TOP CHUTE BLOCKED ALARM | Cyclic in operation | 1 s
SYSTEM_HELP | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_1_PID_FLOW_4 | Real | %DB40.DBD440 | GRATE PID AIR FLOW POINT 4 | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2SW01 | Bool | %DB45.DBX10.2 | CP8 SUPERHEATER SOOTBLOWER 1 RETRACTED PROXIMITY SWITCH | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.SOOTBLOWERS.SHEAT_1_NB_1 | Int | %DB40.DBW1012 | SUPERHEATER SOOTBLOWER 1 NUMBER 1 | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_PID_LAMBDA_MAX | Real | %DB40.DBD216 | STOKER PID AIR LAMBDA MAXIMUM SCALING VALUE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT08.HIHI | Real | %DB41.DBD2272 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4LC02.HIHI | Real | %DB41.DBD1824 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP2_1TS01.HI | Real | %DB41.DBD4 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_PUMP.OP_MAX | Real | %DB40.DBD1878 | OUTPUT MAX VALUE (LMN_HLM) | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.FEED_PUMP.RAMP_ACTV | Bool | %DB42.DBX2010.0 | RAMP ACTIVE | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_PID_FAN_SPD_OUT_4 | Real | %DB40.DBD168 | STOKER PID AIR FAN SPEED OUTPUT 4 | Cyclic in operation | 1 s
3MTR09_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SEND/RECV COOLER 1.RECV.GENERAL.PUMP_STATUS | Int | %DB161.DBW2 | COOLER PUMP STATUS | Cyclic in operation | 1 s
DB SAFETY.RECV.CP2_8_ESPB_OK | Bool | %DB44.DBX2.3 | PUSHFLOOR DELIVERY AREA CP2/8 EM STOP P/BUTTON HEALTHY (1=HEALTHY) | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.OUTPUTS.CP17_5CV01_REF | Real | %DB42.DBD640 | CP17 TURBINE STEAM BLEED TO DEAERATOR VALVE REFERENCE POSITION (4-20mA = 0-100% | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_8LT04.LO | Real | %DB41.DBD1640 | LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP13R4_U113_DP | Real | %DB42.DBD108 | CP13 RACK 4 FILTER 2 DIFFERENTIAL PRESSURE (4..20mA = -10 to +100mBar) | Cyclic in operation | 1 s
IDB GR HYD PUMP 1 PBUS.Status.Load | Real | %DB503.DBD42 | Drive Load in Percentage (%) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2SW07 | Bool | %DB45.DBX11.6 | CP8 BOILER SOOTBLOWER 2 RETRACTED PROXIMITY SWITCH | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.TURBINE_2.CURR_L2 | Real | %DB42.DBD1428 | CURRENT L2 | Cyclic in operation | 1 s
DB SEND/RECV COOLER 3.RECV.ADIABATIC.STATUS | Int | %DB163.DBW30 | ADIABATIC SYSTEM STATUS | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_3TI01b.HI | Real | %DB41.DBD1028 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB MV TURB POWER METER.M6_PAC3200.V3_N | Real | %DB202.DBD8 | VOLTS PHASE 3 TO NEUTRAL (VOLTS) | Cyclic in operation | 1 s
DB MV TURB POWER METER.M6_PAC3200.V2_N | Real | %DB202.DBD4 | VOLTS PHASE 2 TO NEUTRAL (VOLTS) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MAIN_CTRL.STOKER_START | Bool | %DB30.DBX1.7 | START STOKER FEEDERS (FROM SCADA) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.START.BITS.HYD_PWR_PACK_1MTR01 | Bool | %DB30.DBX74.4 | HYDRAULIC POWER PACK | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2PT05.HYST | Real | %DB41.DBD2928 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB SETPOINTS.PID.RECIRC_FAN.GAIN | Real | %DB40.DBD1320 | P TERM (GAIN) | Cyclic in operation | 1 s
DB SETPOINTS.PID.HI_PRESS_CTRL_STEAM.SP | Real | %DB40.DBD1536 | INTERNAL SETPOINT | Cyclic in operation | 1 s
IDB SCND AIR FAN PBUS.Control.RefSpeed | Real | %DB514.DBD40 | Drive Speed Reference in Percentage (%) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_K272 | Bool | %DB45.DBX21.0 | CP13 RACK 4 FILTER 1 INLET VALVE B OPEN SOLENOID 3VAS01b1 | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP2_1TS06.HIHI | Real | %DB41.DBD64 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.PUSH_FLOOR.CP2_1SW31_MIN | Bool | %DB45.DBX2.5 | CP2 PUSH FLOOR LADDER No 2 MINIMUM PROXIMITY | Cyclic in operation | 1 s
DB SEND/RECV COOLER 2.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_LO | Real | %DB162.DBD190 | CIRCULATION WATER OUTLET TEMPERATURE LOW ALARM | Cyclic in operation | 1 s
IDB CP3 ASH SCRAPER DP.Load | Real | %DB529.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.BURNER.GRT_2_TRAV_MIN_TIMEOUT | Int | %DB40.DBW968 | GRATE 2 TRAVERSE MINIMUM TIMEOUT TIME (SEC) | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK2.BEARING_TEMP_7 | DInt | %DB400.DBD124 | TURBINE BEARING TEMPERATURE POS 84.7 DEG C (x100) | Cyclic in operation | 1 s
STRT 1MTR10 | Timer | %T52 | CP3 DISTRIBUTION SCREW START DELAY TIMER | Cyclic in operation | 1 s
DB ALARMS TO SCADA.PROCESS.WORD6 | Int | %DB12.DBW114 | PROCESS ALARMS - WORD 6 | Continuous | 1 s
DB ALARM SETPOINTS.CP13R4_8IN02.HI | Real | %DB41.DBD1220 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP19_2PSZ02 | Real | %DB42.DBD348 | CP19 STEAM DRUM PRESSURE SWITCH H (4-20mA = 0-60 Bar) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.PUSH_FLOOR.CP2_1SW25_MAX | Bool | %DB45.DBX3.6 | CP2 PUSH FLOOR LADDER No 6 MAXIMUM PROXIMITY | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.HIHI.WORD2 | Int | %DB12.DBW24 | HIGH HIGH ALARMS - WORD 2 | Continuous | 1 s
IDB CP13 RS SLEW RING.Status.StatusWord | Int | %DB137.DBW22 | Motor Status Word | Cyclic in operation | 1 s
IDB FEED PUMP 1 PBUS.Control.RefSpeed | Real | %DB508.DBD32 | Drive Speed Reference in Percentage (%) | Cyclic in operation | 1 s
IDB CP3 EN-MASSE CHN CON.Status.StatusWord | Int | %DB106.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_2_PID_FLOW_OUT_3 | Real | %DB40.DBD516 | GRATE PID AIR FLOW OUTPUT 3 | Cyclic in operation | 1 s
IDB FEED PUMP 1 PBUS.Send.ControlWord | Word | %DB508.DBW8 | Control Word | Cyclic in operation | 1 s
DB PROCESS VALUES.EMISSIONS.SO2_Mg_m3 | Real | %DB42.DBD816 | SULPHUR DIOXIDE (Mg/m3) | Continuous | 1 s
DB ALARM SETPOINTS.CP13R4_1FT03.LO | Real | %DB41.DBD1416 | LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_PID_FAN_SPD_OUT_2 | Real | %DB40.DBD264 | STOKER PID AIR FAN SPEED OUTPUT 2 | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_8PT01.LO | Real | %DB41.DBD1672 | LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_S255 | Bool | %DB45.DBX20.3 | CP13 RACK 4 RESIDUE SILO LOADING BELLOWS FULLY RETRACTED PROXIMITY | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TT02.HI | Real | %DB41.DBD3044 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP13R4_1FT03 | Real | %DB42.DBD176 | CP13 RACK 4 SECONDARY AIR FLOW (4..20mA = 0 to 15000 Nm3/H) | Cyclic in operation | 1 s
IDB CP22 EDDY CURR SEP.Rem_Cmds.RemoteCtrl | Bool | %DB104.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.GENERAL.ALL_EQUIP_AVAIL | Bool | %DB30.DBX70.1 | ALL FEED LINE EQUIPMENT AVAILABLE | Cyclic in operation | 1 s
IDB ST HYD PUMP 2 PBUS.Status.Load | Real | %DB501.DBD42 | Drive Load in Percentage (%) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.VALVES.CP8_2SW18 | Bool | %DB45.DBX16.2 | CP8 STEAM DRAIN VALVE 2CV05 CLOSED FEEDBACK | Cyclic in operation | 1 s
STOP PAC DOSING | Timer | %T100 | P.A.C. DOSING SYSTEM STOP DELAY TIMER | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK1.LP_OIL_MIST | DInt | %DB400.DBD32 | LOW PRESSURE OIL MIST mBAR (x100) | Cyclic in operation | 1 s
DB LV GEN POWER METER.KVArh | Real | %DB201.DBD168 | REACTIVE ENERGY USAGE (KVArh) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.BRN_BKUP_CAL_OFFSET | Real | %DB40.DBD388 | BURNER BACKUP VACUUM SENSOR CALIBRATION OFFSET VALUE (mBar) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT09.HIHI | Real | %DB41.DBD2496 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB EMISSIONS DATA.WID_ALARM_COUNT_S | Int | %DB300.DBW170 | WID ALARM COUNTER SECONDS | Cyclic in operation | 1 s
DB LV GEN POWER METER.KVAr2 | Real | %DB201.DBD144 | REACTIVE POWER PHASE 2 (KVAr) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BURNER.GRATE_1_MAN_ST | Bool | %DB1.DBX37.1 | CP3 GRATE 1 TRAVERSE MANUAL START SELECT (SCADA) | Cyclic in operation | 1 s
IDB ST HYD PUMP 3 PBUS.Status.Load | Real | %DB502.DBD42 | Drive Load in Percentage (%) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD3.CP13R4_8UR01 | Bool | %DB11.DBX12.7 | CP13 RACK 4 DeNOx UREA SKID ACTUAL DOSING RATE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4LC02.LO | Real | %DB41.DBD1832 | LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARMS.SYSTEM.WORD1.CP13c_PSSu_HEALTHY | Bool | %DB11.DBX1.4 | CP13c FILTER SAFETYBUS NODE HEALTHY (192.168.2.113) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 6.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_LO | Real | %DB166.DBD190 | CIRCULATION WATER OUTLET TEMPERATURE LOW ALARM | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.HI.WORD1 | Int | %DB12.DBW36 | HIGH ALARMS - WORD 1 | Continuous | 1 s
DB SEND/RECV COOLER 2.SEND.SETPOINTS.FANS_SPEED_MANUAL | Real | %DB162.DBD110 | FANS SPEED FOR REMOTE MANUAL MODE | Cyclic in operation | 1 s
DB PROCESS VALUES.EMISSIONS.DUST_Mg_m3 | Real | %DB42.DBD820 | DUST PARTICULATES (Mg/m3) | Continuous | 1 s
DB SETPOINTS.PID.BOILER_FEED_WATER_VLV.RAMP_EN | Bool | %DB40.DBX1250.2 | RAMP ENABLED (1=ENABLED) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_PID_FAN_SPD_OUT_5 | Real | %DB40.DBD172 | STOKER PID AIR FAN SPEED OUTPUT 5 | Cyclic in operation | 1 s
STOP 1CC02 | Timer | %T45 | CP3 EN-MASSE CHAIN CONVEYOR STOP DELAY TIMER | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.EQUIP_STATUS.ID_FAN_IS_OFF | Bool | %DB30.DBX12.5 | ID FAN IS OFF | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_U113_DP.HIHI | Real | %DB41.DBD864 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
STRT 1CC02 | Timer | %T50 | CP3 EN-MASSE CHAIN CONVEYOR START DELAY TIMER | Cyclic in operation | 1 s
DB ALARMS TO SCADA.COOLERS.COOLER5.WORD2 | Int | %DB12.DBW148 | COOLER 5 ALARMS - WORD 2 | Continuous | 1 s
DB ALARM SETPOINTS.CP13R4_3PI01b.HYST | Real | %DB41.DBD1104 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.HIHI.WORD3 | Int | %DB12.DBW26 | HIGH HIGH ALARMS - WORD 3 | Continuous | 1 s
DB SYSTEM CONTROL.GENERAL.MAIN_CTRL.OP_MODE_0_EN | Bool | %DB30.DBX1.0 | OP MODE 0 (SHUTDOWN) ENABLE | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_PID_FAN_SPD_3 | Real | %DB40.DBD248 | STOKER PID AIR FAN SPEED POINT 3 | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP7_7TT06.HIHI | Real | %DB41.DBD640 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_2_SPD_MANUAL | Real | %DB40.DBD544 | GRATE MANUAL SPEED | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.PRIM_AIR_FLOW_CORR_FACT | Real | %DB40.DBD552 | PRIMARY AIR FLOW CORRECTION FACTOR | Cyclic in operation | 1 s
DB SEND/RECV COOLER 4.RECV.GENERAL.FANS_STATUS | Int | %DB164.DBW4 | COOLER FANS STATUS | Cyclic in operation | 1 s
IDB CP7 LIFT PUMP 2.Rem_Cmds.RunFwd | Bool | %DB183.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_25 | Bool | %DB2.DBX297.0 | Profibus Node | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.FILTER.FILTER1_IN_VLV_B_MD | Bool | %DB1.DBX28.6 | CP13 FILTER 1 INLET VALVE B MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_3 | Bool | %DB2.DBX294.2 | Profibus Node | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_S2652 | Bool | %DB45.DBX23.3 | CP13 RACK 4 RESIDUE SILO LOADING BELLOWS LEVEL SWITCH PADDLE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TT01.HIHI | Real | %DB41.DBD3008 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
IDB CP3 STOKER HYD PMP 3.Rem_Cmds.RemoteCtrl | Bool | %DB114.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.BOILER_2_MD | Bool | %DB1.DBX19.1 | CP8 BOILER SOOTBLOWER 2 MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.FEED_PUMP.PID_ACTV | Bool | %DB42.DBX2010.1 | PID CONTROLLER ACTIVE | Cyclic in operation | 1 s
PrimAirDamper_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP18_1TT09 | Real | %DB42.DBD312 | CP18 SECONDARY AIR DUCT AIR TEMPERATURE PROBE (PT100) (0-400 ºC) | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_TEMP_CTRL.MANUAL_VAL | Real | %DB40.DBD1730 | PID OUTPUT IN MANUAL (MAN) | Cyclic in operation | 1 s
8PU03_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SEND/RECV COOLER 6.RECV.PROCESS_VALUES.CIRC_WATER_OUT_TEMP | Real | %DB166.DBD22 | CIRCULATION WATER OUTLET TEMPERATURE | Cyclic in operation | 1 s
DB SAFETY.RECV.E13c_K433_ON | Bool | %DB44.DBX7.0 | FILTER PANEL CP13c SAFETY CONTACTOR GROUP 1 ENERGISED (1=ON) | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.BURNER.BRN_MAIN_VAC_CAL_VAL | Real | %DB42.DBD1228 | BURNER VACUUM SENSOR 1PT01 CALIBRATED VALUE (mBar) | Cyclic in operation | 1 s
DB MV TURB POWER METER.M6_PAC3200.V3_V1 | Real | %DB202.DBD20 | VOLTS PHASE 3 TO PHASE 1 (VOLTS) | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD1.CP2_SCR_CHN_SND_BLOCK | Bool | %DB11.DBX105.2 | CP2 SCRAPER CHAIN CONVEYOR SECOND DISCHARGE BLOCKED ALARM | Cyclic in operation | 1 s
ID_SHOW | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SCADA DATA.DWORD_DATA.SD_CHLORINE_OUT | Real | %DB45.DBD100 | CHLORINE CONTENT FOR SULPHUR DOSING PLANT | Cyclic in operation | 1 s
DB SETPOINTS.PID.OIL_BURNER.GAIN | Real | %DB40.DBD1688 | P TERM (GAIN) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MAIN_CTRL.EXEC_OVERRIDE | Bool | %DB30.DBX0.3 | SYSTEM EXECUTIVE OVERRIDE MODE REQUEST (FROM SCADA) | Cyclic in operation | 1 s
IDB CP13 RECIRC AIR FAN.Rem_Cmds.RunFwd | Bool | %DB145.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
IDB CP3 STOKER HYD PMP 1.Rem_Cmds.RemoteCtrl | Bool | %DB112.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FEED_LINE.CP18_K92 | Bool | %DB45.DBX6.6 | CP18 STOKER 1 FORWARD RUN RELAY | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FEED_LINE.CP3_1SW04 | Bool | %DB45.DBX6.2 | CP3 SLIDE GATE VALVE OPEN PROXIMITY SWITCH | Cyclic in operation | 1 s
DB SEND/RECV COOLER 5.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_HIHI | Real | %DB165.DBD182 | CIRCULATION WATER OUTLET TEMPERATURE HIGH HIGH ALARM | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_PID_FLOW_OUT_5 | Real | %DB40.DBD212 | STOKER PID AIR FLOW OUTPUT 5 | Cyclic in operation | 1 s
IDB BICARB FEEDER PBUS.Status.ActualSpeed | Real | %DB516.DBD38 | Actual Speed in Percentage (%) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT01.HI | Real | %DB41.DBD2308 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.BURNER.O2_PURGE_ON_TIME | Int | %DB40.DBW970 | O2 METER PURGE ON TIME (DSEC) | Cyclic in operation | 1 s
S9_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
IDB CP13 PAC FEED SCR DP.Status | Int | %DB556.DBW2 | Motor Status | Cyclic in operation | 1 s
IDB CP3 ASH SCRAPER DP.Status | Int | %DB529.DBW2 | Motor Status | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.FILTER.BS_MAINT_VLV_OPN | Bool | %DB1.DBX31.5 | BICARB SILO MAINTENANCE BUTTERFLY VALVE MANUAL OPEN SELECT (SCADA) | Cyclic in operation | 1 s
IDB CP13 BS BLOW FAN.Rem_Cmds.RunFwd | Bool | %DB141.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB SETPOINTS.PID.PRESS_CTRL_STEAM_OUT.INTEGRAL | Int | %DB40.DBW1646 | I TERM (TI) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.DAMPERS.CP13R4_S2651 | Bool | %DB45.DBX30.2 | CP13 RACK 4 PRIMARY AIR DAMPER CLOSED | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2PSZ01.HI | Real | %DB41.DBD2564 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD4.CP17_8LT01 | Bool | %DB11.DBX14.2 | CP17 PLANT WATER TANK LEVEL TRANSDUCER (4-20mA = 0-100%) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.STOKER_SPRINKLER_MD | Bool | %DB1.DBX6.7 | CP3 STOKER SPRINKLER MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.BURNER.OIL_BURNER_STOP_DEL | Int | %DB40.DBW964 | OIL BURNER STOP DELAY TIMER (SEC) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_PID_FLOW_OUT_5 | Real | %DB40.DBD108 | STOKER PID AIR FLOW OUTPUT 5 | Cyclic in operation | 1 s
8MTR05_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB LV GRID POWER METER.KWh | Real | %DB200.DBD164 | ACTIVE ENERGY USAGE (KWh) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.FILTER.ID_FAN_NORMAL_OP_PID_SP | Real | %DB40.DBD676 | ID FANS PID SETPOINT IN NORMAL OPERATION | Cyclic in operation | 1 s
10RMC3F_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_PRDS_CTRL.OP_OFFSET | Real | %DB40.DBD1200 | OUTPUT OFFSET (LMN_OFF) | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP19_2PSZ01 | Real | %DB42.DBD320 | CP19 STEAM DRUM PRESSURE SWITCH HH (4-20mA = 0-60 Bar) | Cyclic in operation | 1 s
3VAS01a1_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.STOP.BITS.FILTER_PLANT | Bool | %DB30.DBX182.4 | BAG FILTER PLANT AND PULSE CONTROLLERS | Cyclic in operation | 1 s
IDB CP3 DISTRIB SCREW.Status.Direction | Bool | %DB110.DBX21.0 | Motor Running Direction (0 = Forward, 1 = Reverse) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.RC_SHUTDOWN_TEMP | Real | %DB40.DBD400 | RESIDENCE CHAMBER SHUTDOWN TEMPERATURE (MODE 9) (DEG C) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_PID_FAN_SPD_1 | Real | %DB40.DBD136 | STOKER PID AIR FAN SPEED POINT 1 | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_PID_FAN_SPD_4 | Real | %DB40.DBD252 | STOKER PID AIR FAN SPEED POINT 4 | Cyclic in operation | 1 s
Filter_Load_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FEED_LINE.CP3_1SW09 | Bool | %DB45.DBX8.4 | CP3 STOKER FUEL/FIRE DAMPER 1CV05 CLOSED POSITION SENSOR | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD5.CP18_1TT03 | Bool | %DB11.DBX17.2 | CP18 RESIDENCE CHAMBER TEMPERATURE PROBE 2 | Cyclic in operation | 1 s
IDB CP13 FILTER 1 HEATER.Rem_Cmds.RemoteCtrl | Bool | %DB135.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SETPOINTS.PID.PRESS_CTRL_STEAM_OUT.SP | Real | %DB40.DBD1628 | INTERNAL SETPOINT | Cyclic in operation | 1 s
DB SAFETY.SEND.IDF1_3FA01_RUNNING | Bool | %DB44.DBX82.3 | 3FA01 ID Fan No.1 Running (PIW500 / DB511.DBX25.1) - 1=Running | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2SW02 | Bool | %DB45.DBX10.3 | CP8 SUPERHEATER SOOTBLOWER 1 EXTENDED PROXIMITY SWITCH | Cyclic in operation | 1 s
DB SETPOINTS.PID.ID_FAN.MANUAL_VAL | Real | %DB40.DBD1270 | PID OUTPUT IN MANUAL (MAN) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2MTR07_REV | Bool | %DB45.DBX13.1 | CP8 ECONOMISER SOOTBLOWER 3 MOTOR RUN REVERSE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2TT05.LOLO | Real | %DB41.DBD3148 | LOW LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.WOOD_FEED.FUEL_DAMPER_STAT | Int | %DB1.DBW182 | FUEL DAMPER STATUS (0 = FAULT, 1 = CLOSED, 2 = OPEN) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD3.CP13R4_SPARE1 | Bool | %DB11.DBX12.1 | CP13 RACK 4 RESIDUE SILO VENT FILTER DIFF PRESSURE | Cyclic in operation | 1 s
IDB CP2 LEV AUGER DP.Load | Real | %DB521.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
DB SETPOINTS.PID.HI_TEMP_CTRL_STEAM.OP_SCALE | Real | %DB40.DBD1518 | OUTPUT SCALE FACTOR (LMN_FAC) | Cyclic in operation | 1 s
IDB FEED PUMP 2 PBUS.Status.ErrorCode | Int | %DB509.DBW46 | Last Trip Code | Cyclic in operation | 1 s
DB SETPOINTS.PID.TEMP_CTRL_STEAM_OUT.CYCLE_TIME | Int | %DB40.DBW1590 | SAMPLE TIME (CYCLE) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.CP8_SOOTB_5_INSERV | Bool | %DB1.DBX21.4 | CP8 SOOTBLOWER 5 IN SERVICE | Cyclic in operation | 1 s
DB PROCESS VALUES.EMISSIONS.O_PCT | Real | %DB42.DBD800 | OXYGEN MEASURED Om (%) | Continuous | 1 s
DB ALARM SETPOINTS.CP13R4_3TI01b.HIHI | Real | %DB41.DBD1024 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
MODE 2 Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
MODE 4 Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FEED_LINE.CP18_1SW15 | Bool | %DB45.DBX8.1 | CP18 STOKER 3 REVERSE PROXIMITY SWITCH | Cyclic in operation | 1 s
IDB CP2 LEV AUGER.Status.StatusWord | Int | %DB103.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD3.CP13R4_1FT02 | Bool | %DB11.DBX13.2 | CP13 RACK 4 PRIMARY AIR FLOW | Cyclic in operation | 1 s
IDB CP7 LP DOSING PMP2.Status.StatusWord | Int | %DB186.DBW22 | Motor Status Word | Cyclic in operation | 1 s
IDB ST HYD PUMP 2 PBUS.Control.RefSpeed | Real | %DB501.DBD32 | Drive Speed Reference in Percentage (%) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MODE_STATUS.EXEC_OPMODE_6_STAT | Int | %DB30.DBW44 | EXECUTIVE OVERRIDE MODE 6 STATUS (0=NOT SEL, 1=REQ, 2=REQ & ACHIEVED) | Cyclic in operation | 1 s
DB SETPOINTS.PID.STOKER_1.GAIN | Real | %DB40.DBD1458 | P TERM (GAIN) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_SPD_FACTOR | Real | %DB40.DBD332 | STOKER SPEED FACTOR | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.SOOTBLOWERS.ECON_3_NB_1 | Int | %DB40.DBW1024 | ECONOMISER SOOTBLOWER 3 NUMBER 1 | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP2_1TS05.HIHI | Real | %DB41.DBD32 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SAFETY.RECV.E13c_K453_ON | Bool | %DB44.DBX5.5 | PRIMARY AIR FAN MOTOR 3MTR10 ISOLATION CONTACTOR (0=ISOLATED) | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_PRDS_CTRL.OP_SCALE | Real | %DB40.DBD1196 | OUTPUT SCALE FACTOR (LMN_FAC) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.FILTER.ID_FAN_SOOTHING_PID_SP | Real | %DB40.DBD680 | ID FANS PID SETPOINT IN SOOTHING OPERATION | Cyclic in operation | 1 s
DB MV TURB POWER METER.KWtot | Real | %DB202.DBD156 | TOTAL ACTIVE POWER (KW) | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_7 | Bool | %DB2.DBX294.6 | Profibus Node | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.SECOND_FAN.CURR_SP | Real | %DB42.DBD1712 | CURRENT RAMP SETPOINT | Cyclic in operation | 1 s
IDB ST HYD PUMP 2 PBUS.Status.ActualSpeed | Real | %DB501.DBD38 | Actual Speed in Percentage (%) | Cyclic in operation | 1 s
DB SAFETY.RECV.CP7_2LSZ02_03 | Bool | %DB44.DBX4.0 | BOILER PANEL CP7 BOILER LOW LOW WATER LEVEL (1=HEALTHY) | Cyclic in operation | 1 s
DB SETPOINTS.PID.PRIM_FAN.OP_SCALE | Real | %DB40.DBD1380 | OUTPUT SCALE FACTOR (LMN_FAC) | Cyclic in operation | 1 s
DB LV GRID POWER METER.KVA2 | Real | %DB200.DBD120 | APPARANT POWER PHASE 2 (KVA) | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.SOOTBLOWERS.RUNS_PER_CYCLE | Int | %DB40.DBW1040 | NUMBER OF RUNS PER CYCLE | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.START.TIMERS.ID_FANS | S5Time | %DB30.DBW150 | MAIN FILTER FANS | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.TURBINE_STEAM_BLEED.RAMP_ACTV | Bool | %DB42.DBX2040.0 | RAMP ACTIVE | Cyclic in operation | 1 s
IDB BICARB FEEDER PBUS.Status.Load | Real | %DB516.DBD42 | Drive Load in Percentage (%) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.SOOTBLOWERS.CP8_2MTR01_FWD | Bool | %DB45.DBX10.0 | CP8 SUPERHEATER SOOTBLOWER 1 MOTOR RUN FORWARD | Cyclic in operation | 1 s
10RMC2F_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_46 | Bool | %DB2.DBX299.5 | Profibus Node | Cyclic in operation | 1 s
PrimFanPID_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_SPARE1.HYST | Real | %DB41.DBD1072 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB ALARMS TO SCADA.PROCESS.WORD5 | Int | %DB12.DBW112 | PROCESS ALARMS - WORD 5 | Continuous | 1 s
IDB CP13 RS HORIZ SCREW.Status.StatusWord | Int | %DB134.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.FILTER.RS_MAINT_VLV_MD | Bool | %DB1.DBX30.4 | RESIDUE SILO MAINTENANCE BUTTERFLY VALVE MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 3.SEND.TIMES.MIN_RUN_TIME | Time | %DB163.DBD214 | COOLER MINIMUM RUN TIME | Cyclic in operation | 1 s
3MTR01_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
IDB CP8 BOILER SOOTBLO 1.Status.StatusWord | Int | %DB119.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP2_1TS01 | Real | %DB42.DBD0 | CP2 HYDRAULIC PUMP MOTOR THERMISTOR (PT100 = 0-150 ºC) | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP18_1PT02 | Real | %DB42.DBD308 | CP18 MOVING GRATE PRESSURE TRANSMITTER 2 (4-20mA = -500-200 mBar) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_PID_FAN_SPD_OUT_5 | Real | %DB40.DBD276 | STOKER PID AIR FAN SPEED OUTPUT 5 | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.BURNER.GRT_2_TRAV_MAX_TIMEOUT | Int | %DB40.DBW956 | GRATE 2 TRAVERSE MAXIMUM TIMEOUT TIME (SEC) | Cyclic in operation | 1 s
CP7 LP AUTO C_OVER OCC | Bool | %M146.3 | CP7 LIFT PUMP AUTO CHANGEOVER OCCURED | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.HI_PRESS_CTRL_STEAM.PID_ACTV | Bool | %DB42.DBX1800.1 | PID CONTROLLER ACTIVE | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_27 | Bool | %DB2.DBX297.2 | Profibus Node | Cyclic in operation | 1 s
DB SYSTEM CONTROL.FILTER.STOP.BITS.BICARB_SYS | Bool | %DB30.DBX182.2 | SODIUM BICARBONATE SILO AND FEED SYSTEM | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_PID_FAN_SPD_5 | Real | %DB40.DBD48 | STOKER PID AIR FAN SPEED POINT 5 | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.HI.WORD2 | Int | %DB12.DBW38 | HIGH ALARMS - WORD 2 | Continuous | 1 s
STRT ASH SYS | Timer | %T111 | ASH CONVEYING AND STORAGE SYSTEM START DELAY TIMER | Cyclic in operation | 1 s
IDB CP13 BS BLOW FAN.Rem_Cmds.RemoteCtrl | Bool | %DB141.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP13R4_8LO01 | Real | %DB42.DBD116 | CP13 RACK 4 BICARB SILO LOAD CELL WEIGHT (4..20mA = xx Tones) | Cyclic in operation | 1 s
DB ALARMS TO SCADA.SUPPLIES.WORD5 | Int | %DB12.DBW94 | POWER SUPPLY ALARMS - WORD 5 | Continuous | 1 s
DB SETPOINTS.PID.OIL_BURNER.CYCLE_TIME | Int | %DB40.DBW1682 | SAMPLE TIME (CYCLE) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 1.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_HYST | Real | %DB161.DBD198 | CIRCULATION WATER OUTLET TEMPERATURE ALARM HYSTERESIS | Cyclic in operation | 1 s
IDB ID FAN B PBUS.Control.RefSpeed | Real | %DB512.DBD40 | Drive Speed Reference in Percentage (%) | Cyclic in operation | 1 s
DB SETPOINTS.PID.BICARB_FEED_HCL.GAIN | Real | %DB40.DBD2102 | P TERM (GAIN) | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.STOP.BITS.ED_CURR_SEP_1GR01 | Bool | %DB30.DBX110.4 | EDDY CURRENT SEPARATOR | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.FILTER.BIC_SILO_VIBRATOR_ON | Bool | %DB1.DBX31.7 | BICARB SILO VIBRATOR MANUAL START SELECT (SCADA) | Cyclic in operation | 1 s
IDB CP2 LEV AUGER DP.Status | Int | %DB521.DBW2 | Motor Status | Cyclic in operation | 1 s
IDB CP3 EN-MASSE CHN CON.Rem_Cmds.RemoteCtrl | Bool | %DB106.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2PSZ01.HYST | Real | %DB41.DBD2576 | ALARM HISTERESYS | Cyclic in operation | 1 s
1MTR16_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD3.CP13R4_3TI01c | Bool | %DB11.DBX12.3 | CP13 RACK 4 FILTER 2 INLET AIR TEMPERATURE | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_PUMP.GAIN | Real | %DB40.DBD1872 | P TERM (GAIN) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FILTER.CP13R4_SB2a | Bool | %DB45.DBX21.4 | CP13 RACK 4 FILTER 2 INLET VALVE A OPENED | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.STOKER_1.CURR_SP | Real | %DB42.DBD1742 | CURRENT RAMP SETPOINT | Cyclic in operation | 1 s
DB PROCESS VALUES.EMISSIONS.NO2_Mg_m3 | Real | %DB42.DBD848 | NITROGEN DIOXIDE NO2 (mg/m3) | Continuous | 1 s
IDB CP13 PAC FEED SCREW.Rem_Cmds.RunFwd | Bool | %DB144.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.HI.WORD3 | Int | %DB12.DBW40 | HIGH ALARMS - WORD 3 | Continuous | 1 s
DB ALARMS TO SCADA.COOLERS.COOLER3.WORD2 | Int | %DB12.DBW140 | COOLER 3 ALARMS - WORD 2 | Continuous | 1 s
3MTR11_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SEND/RECV COOLER 3.SEND.TIMES.ADIABATIC_MIN_RUN_TIME | Time | %DB163.DBD218 | COOLER ADIABATIC SYSTEM MINIMUM RUN TIME | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_PID_FAN_SPD_OUT_2 | Real | %DB40.DBD56 | STOKER PID AIR FAN SPEED OUTPUT 2 | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD3.CP13R4_1FT03 | Bool | %DB11.DBX13.4 | CP13 RACK 4 SECONDARY AIR FLOW | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_U112_DP.HYST | Real | %DB41.DBD848 | ALARM HISTERESYS | Cyclic in operation | 1 s
IDB ST HYD PUMP 1 PBUS.Send.ControlWord | Word | %DB500.DBW8 | Control Word | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK5.ALARM56 | Bool | %DB400.DBX231.0 | CONDENSATE LEVEL MAX MAX | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK3.OIL_COOLER_TEMP | DInt | %DB400.DBD152 | TEMPERATURE OIL COOLER DEG C (POS 87) | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_3_SPD_MAX | Real | %DB40.DBD336 | STOKER MAXIMUM SPEED | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.STOP.BITS.PUSH_FLOOR_1HP01 | Bool | %DB30.DBX110.0 | PUSH FLOOR TRAVEL SOLENOIDS | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_1_PID_FLOW_OUT_5 | Real | %DB40.DBD464 | GRATE PID AIR FLOW OUTPUT 5 | Cyclic in operation | 1 s
8PU01_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP17_4LC02.LOLO | Real | %DB41.DBD1836 | LOW LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.FEED_LINE.CP3_1MTR04_REV | Bool | %DB45.DBX6.1 | CP3 SLIDE VALVE MOTOR RUN REVERSE | Cyclic in operation | 1 s
DB SEND/RECV COOLER 3.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_HYST | Real | %DB163.DBD198 | CIRCULATION WATER OUTLET TEMPERATURE ALARM HYSTERESIS | Cyclic in operation | 1 s
DB SETPOINTS.PID.BICARB_FEED_HCL.OP_MAX | Real | %DB40.DBD2108 | OUTPUT MAX VALUE (LMN_HLM) | Cyclic in operation | 1 s
2MTR03_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.MAIN_CTRL.AUTO_START_EN | Bool | %DB30.DBX0.6 | SYSTEM AUTO START ENABLE (1 = AUTOSTART, 0 = MANUAL) | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.BURNER.ID_START_TIMEOUT | Int | %DB40.DBW942 | ID FAN START TIMEOUT TIME (SEC) | Cyclic in operation | 1 s
IDB CP7 LP DOSING PMP2.Rem_Cmds.RemoteCtrl | Bool | %DB186.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.OP_MODES.OP_MODE_4 | Bool | %DB30.DBX8.4 | SYSTEM IN OPERATION MODE 4 (RAMP-UP) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.ECONOM_2_MD | Bool | %DB1.DBX19.7 | CP8 ECONOMISER SOOTBLOWER 2 MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP2_1TS01.HYST | Real | %DB41.DBD16 | ALARM HISTERESYS | Cyclic in operation | 1 s
S4_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP2_1TS05.HI | Real | %DB41.DBD36 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_2_PID_FLOW_4 | Real | %DB40.DBD188 | STOKER PID AIR FLOW POINT 4 | Cyclic in operation | 1 s
DB SYSTEM CONTROL.WOOD_FEED.STOP.BITS.EN_MASSE_CHN_1MTR09 | Bool | %DB30.DBX110.5 | EN-MASSE CHAIN CONVEYOR | Cyclic in operation | 1 s
3VAS01a2_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.OPN_SHT.WORD1 | Int | %DB12.DBW8 | OPEN/SHORT CIRCUIT ALARMS - WORD 1 | Continuous | 1 s
DB ALARMS.ANALOGUE.LOLO.WORD6.CP19_2LT01 | Bool | %DB11.DBX74.3 | CP19 DP CELL WATER LEVEL | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.PRESS_CTRL_STEAM_OUT.OUTPUT | Real | %DB42.DBD1878 | OUTPUT VALUE | Cyclic in operation | 1 s
DB SETPOINTS.PID.TEMP_CTRL_STEAM_OUT.SP | Real | %DB40.DBD1582 | INTERNAL SETPOINT | Cyclic in operation | 1 s
IDB CP13 PRIM AIR FAN.Rem_Cmds.RunFwd | Bool | %DB146.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.BURNER.CP18_1SW41 | Bool | %DB45.DBX14.3 | CP18 GRATE 1 REVERSE SWITCH 1 | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.FILTER.BS_PULSE_VLV_STAT | Int | %DB1.DBW240 | BICARB SILO PULSE VALVE STATUS | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.POWER.IMPORTING_POWER | Bool | %DB1.DBX10.0 | SITE IS IMPORTING POWER (SCADA) | Cyclic in operation | 1 s
DB SETPOINTS.PID.BOILER_FEED_WATER_VLV.CYCLE_TIME | Int | %DB40.DBW1222 | SAMPLE TIME (CYCLE) | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_33 | Bool | %DB2.DBX298.0 | Profibus Node | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.WOOD_FEED.WOOD_FEED_TIMEOUT_ALM | Int | %DB40.DBW900 | WOOD FEED TIMEOUT ALARM TIME (SEC) | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.BURNER.BRN_TEMP_SENS_SEL | Int | %DB1.DBW150 | BURNER TEMPERATURE SENSOR SELECT (0=LOWEST, 1-3=SENSOR NB 1TT02/03/04, 4=ALL) | Cyclic in operation | 1 s
ALWAYS ON | Bool | %M0.1 | LOGIC 1 FLAG | Cyclic in operation | 1 s
DB ALARMS TO SCADA.LOCAL_ISOL.WORD2 | Int | %DB12.DBW98 | AC MOTOR LOCAL ISOLATOR ALARMS - WORD 2 | Continuous | 1 s
DB SYSTEM CONTROL.FILTER.START.TIMERS.FILTER_PLANT | S5Time | %DB30.DBW154 | BAG FILTER PLANT AND PULSE CONTROLLERS | Cyclic in operation | 1 s
IDB PLC.Profibus.Nodes.Node_29 | Bool | %DB2.DBX297.4 | Profibus Node | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_PID_FAN_SPD_3 | Real | %DB40.DBD40 | STOKER PID AIR FAN SPEED POINT 3 | Cyclic in operation | 1 s
CP2 PS 1SW01 FLT | Bool | %M58.5 | CP2 SCRAPER CHAIN CONVEYOR TENSIONER No 1 FAULT | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BURNER.GRT_2_SPD_MAX | Real | %DB40.DBD536 | GRATE MAXIMUM SPEED | Cyclic in operation | 1 s
IDB CP13 RS INCL SCR DP.Status | Int | %DB559.DBW2 | Motor Status | Cyclic in operation | 1 s
DB SEND/RECV COOLER 2.SEND.ALARM_SETPOINTS.CIRC_WATER_TEMP_HYST | Real | %DB162.DBD198 | CIRCULATION WATER OUTLET TEMPERATURE ALARM HYSTERESIS | Cyclic in operation | 1 s
IDB CP7 PLANT PUMP 1.Status.StatusWord | Int | %DB187.DBW22 | Motor Status Word | Cyclic in operation | 1 s
REC_AIR_FAN_SHOW | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB LV GEN POWER METER.M5_PAC3200.V2_N | Real | %DB201.DBD4 | VOLTS PHASE 2 TO NEUTRAL (VOLTS) | Cyclic in operation | 1 s
DB LV GEN POWER METER.M5_PAC3200.V3_N | Real | %DB201.DBD8 | VOLTS PHASE 3 TO NEUTRAL (VOLTS) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.HI.WORD6.CP19_2PT01 | Bool | %DB11.DBX46.4 | CP19 STEAM DRUM PRESSURE | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.DAMPERS.CP13R4_K2871 | Bool | %DB45.DBX30.3 | CP13 RACK 4 OPEN RECIRCULATION AIR DAMPER | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.PUSH_FLOOR.CP2_1SW24_MAX | Bool | %DB45.DBX3.4 | CP2 PUSH FLOOR LADDER No 5 MAXIMUM PROXIMITY | Cyclic in operation | 1 s
DB MV TURB POWER METER.KVArtot | Real | %DB202.DBD160 | TOTAL REACTIVE POWER (KVAr) | Cyclic in operation | 1 s
DB SETPOINTS.PID.TEMP_CTRL_STEAM_OUT.GAIN | Real | %DB40.DBD1596 | P TERM (GAIN) | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP7_7PLT07 | Real | %DB42.DBD84 | CP7 COOLING CIRCULATION WATER FLOW PRESSURE (4-20mA = 0-5 Bar) | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.HI.WORD4 | Int | %DB12.DBW42 | HIGH ALARMS - WORD 4 | Continuous | 1 s
IDB BICARB FEEDER PBUS.Send.ControlWord | Word | %DB516.DBW8 | Control Word | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD6.CP19_2PT03 | Bool | %DB11.DBX18.6 | CP19 SUPERHEATER 2 STEAM OUTLET PRESSURE | Cyclic in operation | 1 s
IDB CP13 BS BLOW FAN.Status.StatusWord | Int | %DB141.DBW22 | Motor Status Word | Cyclic in operation | 1 s
IDB PLC.DateTime.Sync.Trigger | Bool | %DB2.DBX50.0 | Trigger to Synchronize the System Time of the PLC with HMI | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.TURBINE.ON_GRID | Bool | %DB1.DBX12.0 | TURBINE IS CONNECTED TO GRID | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.SOOTBLOWERS.START_SOOTBLOW_TEMP_CLOS | Real | %DB40.DBD720 | TEMPERATURE SETPOINT TO CLOSE DRAIN VALVE | Cyclic in operation | 1 s
IDB CP3 GRATE HYD PMP 2.Rem_Cmds.RemoteCtrl | Bool | %DB116.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BURNER.GRATE_2_MAN_ST | Bool | %DB1.DBX37.5 | CP3 GRATE 2 TRAVERSE MANUAL START SELECT (SCADA) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD4.CP17_4FT01 | Bool | %DB11.DBX15.5 | CP17 FEEDWATER FLOWMETER (4-20mA = 0-25 t/Hr) | Cyclic in operation | 1 s
DB SETPOINTS.PID.PRESS_CTRL_STEAM_OUT.MAN_AUTO | Bool | %DB40.DBX1664.0 | PID MANUAL/AUTO MODE (1=MANUAL) (MAN_ON) | Cyclic in operation | 1 s
STRT 1MTR01 | Timer | %T54 | CP2 PUSH FLOOR HYDRAULIC POWER PACK START DELAY TIMER | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP13R4_3PI01a | Real | %DB42.DBD120 | CP13 RACK 4 FILTER 1 INLET PRESSURE (4..20mA = 0 - +50mBar) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.PUSH_FLOOR.CP2_1SW30_MIN | Bool | %DB45.DBX2.3 | CP2 PUSH FLOOR LADDER No 1 MINIMUM PROXIMITY | Cyclic in operation | 1 s
IDB CP13 FILT SEAL B DP.Load | Real | %DB550.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.PUSH_FLOOR.CP2_K93 | Bool | %DB45.DBX3.7 | CP2 HYDRAULIC PUMP OFF-LOAD SOLENOID RELAY | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.SOOTBLOWERS.ECON_1_NB_2 | Int | %DB40.DBW1034 | ECONOMISER SOOTBLOWER 1 NUMBER 2 | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT08.HI | Real | %DB41.DBD2276 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.PUSH_FLOOR.TRAV_MAN_MD | Bool | %DB1.DBX2.0 | CP2 PUSH FLOOR TRAVERSE MANUAL MODE SELECT (SCADA) | Cyclic in operation | 1 s
DB ALARMS TO SCADA.PROCESS.WORD8 | Int | %DB12.DBW118 | PROCESS ALARMS - WORD 8 | Continuous | 1 s
DB ALARM SETPOINTS.CP18_1TT07.HYST | Real | %DB41.DBD2256 | ALARM HISTERESYS | Cyclic in operation | 1 s
CP3 1SW17 FLT | Bool | %M64.3 | CP3 SCRAPER CHAIN CONVEYOR TENSION MONITOR 2 FAULT | Cyclic in operation | 1 s
IDB CP13 ID FAN A.Rem_Cmds.RemoteCtrl | Bool | %DB131.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.WOOD_FEED.WOOD_FEED_STOP_DEL | Int | %DB40.DBW898 | WOOD FEED STOP DELAY TIMER (SEC) | Cyclic in operation | 1 s
4CV02_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
1CS01_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
IDB CP21 SULPHUR DOS SYS.Rem_Cmds.RemoteCtrl | Bool | %DB124.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
IDB CP13 FILTER SCREW A.Status.StatusWord | Int | %DB126.DBW22 | Motor Status Word | Cyclic in operation | 1 s
DB SETPOINTS.PID.HI_PRESS_CTRL_STEAM.OP_OFFSET | Real | %DB40.DBD1568 | OUTPUT OFFSET (LMN_OFF) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 5.SEND.GENERAL.REMOTE_RUN | Bool | %DB165.DBX70.7 | 0 = STOP / 1 = RUN | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD1.CP2_HYD_OIL_OVERTEMP | Bool | %DB11.DBX104.1 | CP2 HYDRAULIC OIL OVER TEMPERATURE ALARM | Cyclic in operation | 1 s
IDB CP12 TURBINE COOLER.Rem_Cmds.RunFwd | Bool | %DB172.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD1.CP2_PUSH_FLR_JAMMED | Bool | %DB11.DBX104.2 | CP2 PUSH FLOOR JAMMED ALARM | Cyclic in operation | 1 s
DB SETPOINTS.PID.PRIM_FAN.RAMP_RATE | Real | %DB40.DBD1356 | RAMP TO SETPOINT RATE | Cyclic in operation | 1 s
DB SYSTEM CONTROL.GENERAL.EQUIP_STATUS.PRIM_FAN_IS_OFF | Bool | %DB30.DBX12.6 | PRIMARY AIR FAN IS OFF | Cyclic in operation | 1 s
IDB CP13 BS BLOW FAN DP.Status | Int | %DB553.DBW2 | Motor Status | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.PUSH_FLOOR.CP2_1SW20_MAX | Bool | %DB45.DBX2.4 | CP2 PUSH FLOOR LADDER No 1 MAXIMUM PROXIMITY | Cyclic in operation | 1 s
MODE 1 Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.FILTER.BS_PULSE_VLV_OPN | Bool | %DB1.DBX31.3 | BICARB SILO HOPPER PULSE VALVE MANUAL OPEN SELECT (SCADA) | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.FILTER.BS_MAINT_VLV_STAT | Int | %DB1.DBW238 | BICARB SILO MAINTENANCE VALVE STATUS | Cyclic in operation | 1 s
IDB CP2 HYD PUMP HTR.Status.StatusWord | Int | %DB102.DBW22 | Motor Status Word | Cyclic in operation | 1 s
8MTR04_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP7_7TT06 | Real | %DB42.DBD80 | CP7 COOLING CIRCULATION WATER RETURN TEMPERATURE (4-20mA = 0-150 ºC) | Cyclic in operation | 1 s
DB ALARMS.ANALOGUE.OPN_SHT.WORD6.CP19_2PSZ01 | Bool | %DB11.DBX18.0 | CP19 STEAM DRUM PRESSURE SWITCH HH | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_PRDS_CTRL.OP_MAX | Real | %DB40.DBD1188 | OUTPUT MAX VALUE (LMN_HLM) | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.WOOD_FEED.STK_1_STATUS | Int | %DB1.DBW168 | CP3 STOKER 1 SOLENOIDS STATUS (SCADA DISPLAY) | Cyclic in operation | 1 s
Warning_Popup1 | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.BURNER.PRIM_DAMPER_OPN | Bool | %DB1.DBX38.1 | CP13 PRIMARY AIR DAMPER MANUAL OPEN SELECT (SCADA) | Cyclic in operation | 1 s
DB ALARMS TO SCADA.ANALOGUE.LOLO.WORD4 | Int | %DB12.DBW70 | LOW LOW ALARMS - WORD 4 | Continuous | 1 s
IDB CP13 SECON AIR FAN.Rem_Cmds.RemoteCtrl | Bool | %DB147.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB LV GRID POWER METER.M4_PAC3200.V3_V1 | Real | %DB200.DBD20 | VOLTS PHASE 3 TO PHASE 1 (VOLTS) | Cyclic in operation | 1 s
DB SCADA DATA.BIT_DATA.DAMPERS.CP13R4_S2641 | Bool | %DB45.DBX30.5 | CP13 RACK 4 RECIRCULATION AIR DAMPER CLOSED | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.WOOD_FEED.STK_3_TRAV_INTERVAL | Int | %DB40.DBW888 | STOKER 3 TRAVERSE INTERVAL TIME (SEC) | Cyclic in operation | 1 s
IDB CP3 STOKER HYD PMP 2.Rem_Cmds.RemoteCtrl | Bool | %DB113.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK3.WHEEL_TEMP | DInt | %DB400.DBD148 | TURBINE BLADE WHEEL TEMPERATURE DEG C (x100) | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP18_1TT09.HYST | Real | %DB41.DBD2512 | ALARM HISTERESYS | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK5.ALARM113 | Bool | %DB400.DBX238.1 | CONDENSATE PUMP 1 RUNNING | Cyclic in operation | 1 s
DB MISCELLANEOUS.INTEGERS.BURNER.O2_PURGE_VLV_STAT | Int | %DB1.DBW158 | CP19 O2 PURGE VALVE STATUS (0 = FAULT, 1 = CLOSED, 2 = OPEN) | Cyclic in operation | 1 s
DB SETPOINTS.PID.TURBINE_STEAM_BLEED.RAMP_RATE | Real | %DB40.DBD1908 | RAMP TO SETPOINT RATE | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.SECOND_AIR_FAN.O2_PID_O2_SP_1 | Real | %DB40.DBD752 | SECONDARY AIR FAN PID CONTROLLER O2 SETPOINT 1 | Cyclic in operation | 1 s
MODE 9 Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.BURNER.MODE9_SECONDS | Real | %DB42.DBD1260 | BURNER MODE 9 COUNTDOWN TIME - SECONDS | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_8LO01.HIHI | Real | %DB41.DBD928 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
IDB CP13 RS HORIZ SCR DP.Load | Real | %DB560.DBD4 | Motor Load in Percentage (%) | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.BURNER.MODE9_MINUTES | Real | %DB42.DBD1256 | BURNER MODE 9 COUNTDOWN TIME - MINUTES | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.BOILER_2_EXT | Bool | %DB1.DBX19.2 | CP8 BOILER SOOTBLOWER 2 MANUAL EXTEND SELECT (SCADA) | Cyclic in operation | 1 s
IDB CP6 WATER TREATMENT.Rem_Cmds.RemoteCtrl | Bool | %DB189.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP13R4_1TT10 | Real | %DB42.DBD172 | CP13 RACK 4 PRIMARY AIR TEMPERATURE (4..20mA = 0 to 400ºC) | Cyclic in operation | 1 s
DB SEND/RECV COOLER 1.RECV.GENERAL.WATCHDOG | Bool | %DB161.DBX0.0 | <No Value> | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_U112_DP.HIHI | Real | %DB41.DBD832 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP19_2PT05.HIHI | Real | %DB41.DBD2912 | HIGH HIGH ALARM SETPOINT | Cyclic in operation | 1 s
IDB CP13 BS FEED SCREW.Rem_Cmds.RunFwd | Bool | %DB140.DBX18.1 | 0 = Stop / 1 = Run Forward | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.TURBINE.STEAM_PRESS | Real | %DB42.DBD1120 | TURBINE LIVE STEAM PRESSURE | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_1TT10.HI | Real | %DB41.DBD1380 | HIGH ALARM SETPOINT | Cyclic in operation | 1 s
DB CP12 TURBINE.BLOCK5.ALARM60 | Bool | %DB400.DBX231.4 | CONDENSATE LEVEL MIN | Cyclic in operation | 1 s
IDB CP12 TURBINE COOLER.Rem_Cmds.RemoteCtrl | Bool | %DB172.DBX18.0 | 0 = Local Control / 1 = Remote Control | Cyclic in operation | 1 s
DB PROCESS VALUES.MISCELLANEOUS.TURBINE.WINDING_TEMP_V | Real | %DB42.DBD1144 | WINDING TEMPERATURE V | Cyclic in operation | 1 s
DB SETPOINTS.PID.HI_TEMP_CTRL_STEAM.CYCLE_TIME | Int | %DB40.DBW1498 | SAMPLE TIME (CYCLE) | Cyclic in operation | 1 s
DB ALARMS.PROCESS.WORD1.CP2_HYD_OIL_LVL_LO | Bool | %DB11.DBX104.0 | CP2 HYDRAULIC OIL LEVEL LOW ALARM | Cyclic in operation | 1 s
DB ALARM SETPOINTS.CP13R4_1FT03.LOLO | Real | %DB41.DBD1420 | LOW LOW ALARM SETPOINT | Cyclic in operation | 1 s
DB PROCESS VALUES.PID.SECOND_FAN.PID_ACTV | Bool | %DB42.DBX1710.1 | PID CONTROLLER ACTIVE | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.SOOTBLOWERS.CP8_SOOTB_6_INSERV | Bool | %DB1.DBX21.5 | CP8 SOOTBLOWER 6 IN SERVICE | Cyclic in operation | 1 s
DB SETPOINTS.TIMERS.BURNER.COOLING_TIME_M | Int | %DB40.DBW946 | BURNER COOLING TIME PERIOD (COOLING - MODE 9) (MINUTES) | Cyclic in operation | 1 s
STRT BICARB SYS | Timer | %T113 | SODIUM BICARBONATE SILO AND FEED SYSTEM START DELAY TIMER | Cyclic in operation | 1 s
DB LV GRID POWER METER.M4_PAC3200.V3_N | Real | %DB200.DBD8 | VOLTS PHASE 3 TO NEUTRAL (VOLTS) | Cyclic in operation | 1 s
2CV02PressPID_Popup | Bool | <No Value> | <No Value> | Cyclic in operation | 1 s
DB ALARMS TO SCADA.PROFIBUS.WORD2 | Int | %DB12.DBW4 | PROFIBUS ALARMS - WORD 2 | Continuous | 1 s
DB SETPOINTS.SETPOINT.WOOD_FEED.STK_1_PID_FLOW_2 | Real | %DB40.DBD76 | STOKER PID AIR FLOW POINT 2 | Cyclic in operation | 1 s
DB ALARMS TO SCADA.SYSTEM.WORD1 | Int | %DB12.DBW0 | SYSTEM ALARMS - WORD 1 | Continuous | 1 s
IDB REC AIR FAN PBUS.Status.ActualSpeed | Real | %DB515.DBD46 | Actual Speed in Percentage (%) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.STK_2_PID_MTHD_3_SEL | Bool | %DB1.DBX8.0 | STOKER 2 PID CONTROLLER METHOD 3 SELECTED | Cyclic in operation | 1 s
DB SETPOINTS.SETPOINT.BOILER.CP7_LIFT_PUMP_START_SP | Real | %DB40.DBD632 | FEED WATER TANK WATER LEVEL TO START LIFT PUMP SETPOINT (%) | Cyclic in operation | 1 s
DB MISCELLANEOUS.BITS.WOOD_FEED.DIST_SCREW_ROT_SENS_OFF | Bool | %DB1.DBX4.3 | CP3 DISTRIBUTION SCREW ROTATION SENSOR DISABLE (SCADA) | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP17_2FT01 | Real | %DB42.DBD252 | CP17 SUPERHEATER 2 FLOW METER STEAM OUTLET (4-20mA = 0-25000 Kg/Hr) | Cyclic in operation | 1 s
DB PROCESS VALUES.ANALOGUE.INSTRUMENTS.CP13R4_8IN02 | Real | %DB42.DBD152 | CP13 RACK 4 RESIDUE SILO HEPA FILTER PRESSURE (4..20mA = 0 - +50mBar) | Cyclic in operation | 1 s
DB LV GRID POWER METER.M4_PAC3200.V2_V3 | Real | %DB200.DBD16 | VOLTS PHASE 2 TO PHASE 3 (VOLTS) | Cyclic in operation | 1 s
DB SETPOINTS.PID.FEED_WTR_TANK_PRDS_CTRL.MAN_AUTO | Bool | %DB40.DBX1204.0 | PID MANUAL/AUTO MODE (1=MANUAL) (MAN_ON) | Cyclic in operation | 1 s

## Multiplexing
HMI Tag name | Multiplex Tag | Index